## Original
Matiari—Lahore ±660kV HVDC Project The Schedule for Monpolar Pole 1, Pole 2 and Bipole System Commissioning Tests - Reversed Power Direction & High Power Test
Precondition for Reversed Power Direction & High Power Test
NTDC: 1. Jamshore II / Dadu New / Port Qasim (2 lines) are both connected to Matiari CS ( totally 8 lines connection) 2. All the SCS equipment take into running. 3. Major IPPs including Engro Thar / China Hubo / SAHIWAL PSS should put into service. 4. The reactor formerly connected on the Engro Thar-Jamshoro line at Jamshoro be moved from Jamshoro to Engro Thar and connected on the second Matiari- Engro Thar line.（Optional）
Sr. No. | Commissioning items | Mode | Items designations | Sub-item designation | Test Date | Tentative Date | Pole Power
(MW)
Pole 1 DC Station Tests, Matiari
1 | 2.3.1 | n.a. | Station Tests | Pole1 Electrical- Magnetic Interference Test |  |  | -
2 | 3.3.1 | n.a. | Station Tests | Pole 1 DC switching sequence |  |  | -
3 | 4.3.1 | n.a. | Station Tests | Pole 1 ESOF |  |  | -
4 | 4.3.2 | n.a. | Station Tests | Pole 1 simulate Converter Transformer Gas buchholz Protection |  |  | -
5 | 5.3.1 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 1 |  |  | -
6 | 6.3.1 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 1 |  |  | -
7 | 7.3.1 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 1 |  |  | -
8 | 7.3.2 | n.a. | Station Tests | Open Line Test with DC Line, Autol Mode, Pole 1 |  |  | -
Pole 2 DC Station Tests, Lahore
9 | 2.3.2 | n.a. | Station Tests | Pole2 Electrical- Magnetic Interference Test |  |  | -
10 | 3.3.2 | n.a. | Station Tests | Pole 2 DC switching sequence |  |  | -
11 | 4.3.3 | n.a. | Station Tests | Pole 2 ESOF |  |  | -
12 | 4.3.4 | n.a. | Station Tests | Pole 2 simulate Converter Transformer Gas buchholz Protection |  |  | -
13 | 5.3.2 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 2 |  |  | -
14 | 6.3.2 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 2 |  |  | -
15 | 7.3.3 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 2 |  |  | -
16 | 7.3.4 | n.a. | Station Tests | Open Line Test with DC Line, Auto Mode, Pole 2 |  |  | -
Pole 1 DC Station Tests, Lahore
17 | 2.3.1 | n.a. | Station Tests | Pole1 Electrical- Magnetic Interference Test |  |  | -
18 | 3.3.1 | n.a. | Station Tests | Pole 1 DC switching sequence |  |  | -
19 | 4.3.1 | n.a. | Station Tests | Pole 1 ESOF |  |  | -
20 | 4.3.2 | n.a. | Station Tests | Pole 1 simulate Converter Transformer Gas buchholz Protection |  |  | -
21 | 5.3.1 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 1 |  |  | -
22 | 6.3.1 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 1 |  |  | -
23 | 7.3.1 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 1 |  |  | -
24 | 7.3.2 | n.a. | Station Tests | Open Line Test with DC Line, Autol Mode, Pole 1 |  |  | -
Pole 2 DC Station Tests, Matiari
26 | 3.3.2 | n.a. | Station Tests | Pole 2 DC switching sequence |  |  | -
27 | 4.3.3 | n.a. | Station Tests | Pole 2 ESOF |  |  | -
28 | 4.3.4 | n.a. | Station Tests | Pole 2 simulate Converter Transformer Gas buchholz Protection |  |  | -
29 | 5.3.2 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 2 |  |  | -
30 | 6.3.2 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 2 |  |  | -
31 | 7.3.3 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 2 |  |  | -
32 | 7.3.4 | n.a. | Station Tests | Open Line Test with DC Line, Autol Mode, Pole 2 |  |  | -
Pole1 Low Power System Test - Reversed Power Direction
1 | 11.3.1 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Start/Stop Pole | Day1 |  | 200
2 | 11.3.2 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Control System Switchover | Day1 |  | 200
3 | 11.3.3 | GR/MR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Ground/Metallic Return Transfer | Day1 |  | 200
4 | 12.3.1 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Start/Stop Pole, Joint Power Control | Day1 |  | 200
5 | 12.3.2 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Control System Switchover | Day1 |  | 200
Pole2 Low Power System Test- Reversed Power Direction
6 | 11.3.1 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Start/Stop Pole | Day1 |  | 200
7 | 11.3.2 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Control System Switchover | Day1 |  | 200
8 | 11.3.3 | GR/MR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Ground/Metallic Return Transfer | Day1 |  | 200
9 | 12.3.1 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Start/Stop Pole, Joint Power Control | Day1 |  | 200
10 | 12.3.2 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Control System Switchover | Day1 |  | 200
Bipole Low Power System Test- Reversed Power Direction
11 | 10.3.1 | BPGR | Initial Operation Tests, Reversed Power Direction | Start/Stop Bipole | Day2 |  | 400
12 | 10.3.2 | BPGR | Initial Operation Tests, Reversed Power Direction | Control System Switchover | Day2 |  | 400
13 | 11.3.1 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip X in Rectifier with Telecommunication | Day2 |  | 400
14 | 11.3.2 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip Y in Inverter with Telecommunication | Day2 |  | 400
15 | 11.3.3 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip Z in Rectifier with Telecommunication | Day2 |  | 400
16 | 12.3.1 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Power Ramping | Day2 |  | 800
17 | 12.3.2 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Operation, Pole 2 Power Ramping with/without Telecommunication | Day2 |  | 600
18 | 12.3.2 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Operation, Pole 1 Power Ramping with/without Telecommunication | Day2 |  | 600
19 | 12.3.3 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Simulated Pole1 DC Line Fault（only Lahore） | Day2 |  | 400
20 | 12.3.4 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Simulated Pole2 DC Line Fault（only Lahore） | Day2 |  | 400
21 | 13.3.5 | BPGR | DC Line Faults | DC Line Faults at Pole 1 near Rectifier, Reverse Power Direction(Optional) | Day2 |  | 400
22 | 13.3.6 | BPGR | DC Line Faults | DC Line Faults at Pole 2 near Inverter, Reverse Power Direction(Optional) | Day2 |  | 400
Pole1 High Power Tests, Normal Power Direction------ A5
1 | 2.3.1 | GR | Pole 1 High Power Test, | Pole Start | Day3 |  | 200
2 | 2.3.2 | GR | Pole 1 High Power Test | Power Ramp | Day3 |  | 200-2000
3 | 2.3.3 | GR | Pole 1 High Power Test | Tap Changer Control, Manual Tap Changer Step | Day3 |  | 2000
4 | 2.3.4 | GR /MR | Pole 1 High Power Test | Ground/Metallic Return Transfer | Day3 |  | 2000
5 | 3.3.1 | BPGR | Pole 1 Heat Run Test and Special Measurements | Pole 1 Run at 1.00 p.u. in Monopole without Redundant Cooling | Day3 |  | 2200
6 | 3.3.2 | BPGR | Pole 1 Heat Run Test and Special Measurements | Pole 1 Run at 1.1 p.u. in Monopole with Redundant Cooling | Day3 |  | 2400
7 | 3.3.3 | BPGR | Pole 1 Heat Run Test and Special Measurements | Radio Interference Measurements | Day3 |  | 2200/2400
8 | 3.3.4 | BPGR | Pole 1 Heat Run Test and Special Measurements | Audible Noise Check | Day3 |  | 2200/2400
9 | 3.3.5 | BPGR | Pole 1 Heat Run Test and Special Measurements | Station Service Power Losses | Day3 |  | 2200/2400
10 | 3.3.6 | BPGR | Pole 1 Heat Run Test and Special Measurements | Temperature Measurement With IR-Camera Equipment | Day3 |  | 2200/2400
11 | 3.3.7 | BPGR | Pole 1 Heat Run Test and Special Measurements | Ground Electrode Test Program | Day3 |  | 2200/2400
Pole2 High Power Tests, Normal Power Direction
12 | 4.3.1 | GR | Pole 2 High Power Test, | Pole Start | Day4 |  | 200
13 | 4.3.2 | GR | Pole 2 High Power Test | Power Ramp | Day4 |  | 200-2000
14 | 4.3.3 | BPGR | Pole 2 High Power Test | Tap Changer Control, Manual Tap Changer Step | Day4 |  | 2400
15 | 5.3.1 | BPGR | Pole 2 Heat Run Test and Special Measurements | Pole 2 Run at 1.00 p.u. in Monopole without Redundant Cooling | Day4 |  | 2400
16 | 5.3.2 | BPGR | Pole 2 Heat Run Test and Special Measurements | Pole 2 Run at 1.1 p.u. in Monopole with Redundant Cooling | Day4 |  | 2400
17 | 5.3.3 | BPGR | Pole 2 Heat Run Test and Special Measurements | Radio Interference Measurements | Day4 |  | 2200/2400
18 | 5.3.4 | BPGR | Pole 2 Heat Run Test and Special Measurements | Audible Noise Check | Day4 |  | 2200/2400
19 | 5.3.5 | BPGR | Pole 2 Heat Run Test and Special Measurements | Station Service Power Losses | Day4 |  | 2200/2400
20 | 5.3.6 | BPGR | Pole 2Heat Run Test and Special Measurements | Temperature Measurement With IR-Camera Equipment | Day4 |  | 2200/2400
21 | 5.3.7 | BPGR | Pole 2Heat Run Test and Special Measurements | Fault in Pole 1 Running at High Power with Pole 2 at minimum in Pole Power Control | Day4 |  | 2000/2200
Start the Trial Run Operation ( High Power-stage 1）
1 |  |  | Trial Run Operation(168 hours) - high power | Capability Demonstration Test ( 6 hours) | Day 5-11 |  | 2000
The HVDC project get into Trial Run Operation( High Power-stage 1）
Bipole Rated Load Operation, Normal Power Direction (Optional,depend on system condition)
1 | 2.3.1 | BPGR | Bipole Rated Load Operation | Bipole Power Ramping | TBD |  | 400-4000
2 | 2.3.2 | BPGR | Bipole Rated Load Operation | Heat Run Test at 1.00 p.u. | TBD |  | 4000
3 | 2.3.3 | BPGR | Bipole Rated Load Operation | Radio Interference Measurements | TBD |  | 4000
4 | 2.3.4 | BPGR | Bipole Rated Load Operation | Audible Noise Check | TBD |  | 4000
5 | 2.3.5 | BPGR | Bipole Rated Load Operation | Station Service Power Losses | TBD |  | 4000
6 | 2.3.6 | BPGR | Bipole Rated Load Operation | Temperature Measurement With IR-Camera Equipment | TBD |  | 4000
Pole1 High Power Test, Reversed Power Direction (Optional,depend on system condition)
1 | 6.3.1 | GR | Pole1 High Power Test | Pole Start | TBD |  | 200
2 | 6.3.2 | GR | Pole1 High Power Test | Power Ramp | TBD |  | 1000
Bipole High Power Operation, Reversed Power Direction (Optional,depend on system condition)
3 | 3.3.1 | BPGR | Bipole High Power Operation | Bipole Power Ramping | TBD |  | 2000

## NPCC detail (A1-A2-A3-A4-A5-A6) (hidden)
Matiari—Lahore ±660kV HVDC Project The Schedule for Monopolar Pole 1, Pole 2 and Bipole System Commissioning Tests
Sr. No. | Test Block | Commissioning Items | Mode | Item Designations | Sub-item Designation | Test Date | Power imported from AC Network
(MW)
DC Monopolar Station Tests-No Power Transfer
All tests in Test Block - S1, S2, S3, S4 should be executed in sequence as mentioned below. If any test fails in one block, next test item in the same block should not be executed. However, jump to other Test Blocks (Test Block-S1, S2, S3, S4) can be performed.
Pole 1 DC Station Tests, Matiari
1 | Test Block-S1 | 2.3.1 | n.a. | Station Tests | Pole1 Electrical- Magnetic Interference Test | Day1 | -
2 |  | 3.3.1 | n.a. | Station Tests | Pole 1 DC switching sequence |  | -
3 |  | 4.3.1 | n.a. | Station Tests | Pole 1 ESOF |  | -
4 |  | 4.3.2 | n.a. | Station Tests | Pole 1 simulate Converter Transformer Gas buchholz Protection |  | -
5 |  | 5.3.1 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 1 |  | -
6 |  | 6.3.1 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 1 |  | -
7 |  | 7.3.1 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 1 |  | -
8 |  | 7.3.2 | n.a. | Station Tests | Open Line Test with DC Line, Autol Mode, Pole 1 |  | -
Pole 2 DC Station Tests, Lahore
9 | Test Block-S2 | 2.3.2 | n.a. | Station Tests | Pole2 Electrical-Magnetic Interference Test | Day1 | -
10 |  | 3.3.2 | n.a. | Station Tests | Pole 2 DC switching sequence |  | -
11 |  | 4.3.3 | n.a. | Station Tests | Pole 2 ESOF |  | -
12 |  | 4.3.4 | n.a. | Station Tests | Pole 2 simulate Converter Transformer Gas buchholz Protection |  | -
13 |  | 5.3.2 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 2 |  | -
14 |  | 6.3.2 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 2 |  | -
15 |  | 7.3.3 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 2 |  | -
16 |  | 7.3.4 | n.a. | Station Tests | Open Line Test with DC Line, Autol Mode, Pole 2 |  | -
Pole 1 DC Station Tests, Lahore
17 | Test Block-S3 | 2.3.1 | n.a. | Station Tests | Pole1 Electrical-Magnetic Interference Test | Day2 | -
18 |  | 3.3.1 | n.a. | Station Tests | Pole 1 DC switching sequence |  | -
19 |  | 4.3.1 | n.a. | Station Tests | Pole 1 ESOF |  | -
20 |  | 4.3.2 | n.a. | Station Tests | Pole 1 Simulate Converter Transformer Gas buchholz Protection |  | -
21 |  | 5.3.1 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 1 |  | -
22 |  | 6.3.1 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 1 |  | -
23 |  | 7.3.1 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 1 |  | -
24 |  | 7.3.2 | n.a. | Station Tests | Open Line Test with DC Line, Autol Mode, Pole 1 |  | -
Pole 2 DC Station Tests, Matiari
17 | Test Block-S4 | 2.3.1 | n.a. | Station Tests | Pole2 Electrical- Magnetic Interference Test | Day2 | -
26 |  | 3.3.2 | n.a. | Station Tests | Pole 2 DC switching sequence |  | -
27 |  | 4.3.3 | n.a. | Station Tests | Pole 2 ESOF |  | -
28 |  | 4.3.4 | n.a. | Station Tests | Pole 2 simulate Converter Transformer Gas buchholz Protection |  | -
29 |  | 5.3.2 | n.a. | Station Tests | Energization of Blocked Valve Group, Pole 2 |  | -
30 |  | 6.3.2 | n.a. | Station Tests | Open Line Test without DC Line, Manual Mode, Pole 2 |  | -
31 |  | 7.3.3 | n.a. | Station Tests | Open Line Test with DC Line, Manual Mode, Pole 2 |  | -
32 |  | 7.3.4 | n.a. | Station Tests | Open Line Test with DC Line, Auto Mode, Pole 2 |  | -
DC Monopolar Point to Point Tests-Low Power
DC Station Tests must be successful before starting these tests
All tests in Test Block-LP1, LP2 should be executed in sequence as mentioned below. If any test fails in one block, next test item in the same block should not be executed however, next test block (Test Block-LP1,LP2) can be executed in the listed sequence.
Pole1 Low Power System Test, Normal Power Direction
Ground return mode
33 | Test Block-LP1 | 2.3.1 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block | Day3 | 200
34 |  | 2.3.2 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop |  | 200
35 |  | 2.3.3 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover |  | 200
36 |  | 2.3.4 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check |  | 200
37 |  | 2.3.5 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check |  | 200
38 |  | 2.3.6 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | AC Side Protections, Analogue Input Check |  | 200
Metallic return mode
39 |  | 2.4.1 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block |  | 200
40 |  | 2.4.2 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop |  | 200
41 |  | 2.4.3 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover |  | 200
42 |  | 2.4.4 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check |  | 200
43 |  | 2.4.5 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check |  | 200
Pole2 Low Power System Test, Normal Power Direction
Ground return mode
44 | Test Block-LP2 | 2.3.1 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block | Day3 | 200
45 |  | 2.3.2 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop |  | 200
46 |  | 2.3.3 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover |  | 200
47 |  | 2.3.4 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check |  | 200
48 |  | 2.3.5 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check |  | 200
49 |  | 2.3.6 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | AC Side Protections, Analogue Input Check |  | 200
Metallic return mode
50 |  | 2.4.1 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block |  | 200
51 |  | 2.4.2 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop |  | 200
52 |  | 2.4.3 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover |  | 200
53 |  | 2.4.4 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check |  | 200
54 |  | 2.4.5 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check |  | 200
DC Monopolar Low Power Protective Trip Testing
DC Tests from Sr. No. 33-54 must be successful before starting these tests
All tests in Test Block-LP3, LP4 may/may not be executed in sequence as mentioned below. If any test fails in one block, next test item in the same block can be executed however next test block (Test Block-LP4) cannot be executed until sucessful execution of Test Block 3.
Pole1 Low Power System Test
55 | Test Block-LP3 | 3.3.1 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip X in Rectifier with Telecommunication | Day4 | 200
56 |  | 3.3.2 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Rectifier with Telecommunication |  | 200
57 |  | 3.3.3 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Z in Rectifier with Telecommunication |  | 200
58 |  | 3.3.4 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip X in Inverter with Telecommunication |  | 200
59 |  | 3.3.5 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Inverter with Telecommunication |  | 200
60 |  | 3.3.6 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Z in Inverter with Telecommunication |  | 200
61 |  | 3.3.7 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Rectifier without Telecommunication |  | 200
62 |  | 3.3.8 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Inverter without Telecommunication |  | 200
63 |  | 3.3.9 | GR | Protective Trip X, Y, and Z, Normal Power Direction | VBE Fault Protection Trip – Rectifier |  | 200
64 |  | 3.3.10 | GR | Protective Trip X, Y, and Z, Normal Power Direction | VBE Fault Protection Trip – Inverter |  | 200
65 |  | 4.3.1 | GR | System Supervision and Switchover | Active System Power Failure |  | 200
66 |  | 4.3.2 | GR | System Supervision and Switchover | Profibus bus Failure |  | 200
67 |  | 4.3.3 | GR | System Supervision and Switchover | LAN Bus Failure |  | 200
68 | Test Block-LP4 | 5.3.1 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Current Ramping and Hold on |  | 530
69 |  | 5.3.2 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | System Switchover and Telecommunication Failure During Current Ramping |  | 330
70 |  | 5.3.3 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Tap Changer Control, Manual Tap Changer Stepping |  | 200
71 |  | 5.3.4 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Current Step Test | Day4 | 330
72 |  | 5.3.5 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Voltage Step Test |  | 330
73 |  | 5.3.6 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Angle γ Step Test |  | 330
74 |  | 5.3.7 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Control Mode Shift, Current Margin Compensation |  | 330
75 |  | 6.3.1 | GR | Steady State Operation, Joint power Control, Normal Power Direction | Start/Stop Pole |  | 200
76 |  | 6.3.2 | GR | Steady State Operation, Joint power Control, Normal Power Direction | System Switchover and Telecommunication Failure During Power Ramping |  | 500
77 |  | 6.3.3 | GR | Steady State Operation, Joint power Control, Normal Power Direction | Power Step Test |  | 400
78 |  | 6.3.4 | GR | Steady State Operation, Joint power Control, Normal Power Direction | Control Mode Shift, Current Margin Compensation |  | 400
Monopolar Low Power Operational Tests
DC Tests from Sr. No. 55-78 must be successful before starting these tests
All tests in Test Block-LP5, LP6, LP7, LP8 should be executed in sequence as listed below. If any test fails in one block, next test item in the same block should not be executed however, next test block (Test Block-LP5,LP6,L LP7,LP8) can be executed in the listed sequence.
79 | Test Block-LP5 | 7.3.1 | GR | Normal Operation, Separate Current Control without Telecommunication | Start/Stop Pole | Day5 | 200
80 |  | 7.3.2 | GR | Normal Operation, Separate Current Control without Telecommunication | System Switchover During Current Ramp |  | 330
81 |  | 8.3.1 | GR | Normal/Reduced Voltage, Normal Power Direction | Manual/Protection Triggering Reduced Voltage |  | 200
82 |  | 8.3.2 | GR | Normal/Reduced Voltage, Normal Power Direction | Power/Current Ramp |  | 400
83 | Test Block-LP6 | 9.3.1 | GR | Reactive Power Control, Normal Power Direction | Filter Requirement |  | 750
84 |  | 9.3.2 | GR | Reactive Power Control, Normal Power Direction | Filter Replacement |  | 200
85 |  | 9.3.3 | GR | Reactive Power Control, Normal Power Direction | Reactive Power Control |  | 400
86 |  | 9.3.4 | GR | Reactive Power Control, Normal Power Direction | Voltage Control |  | 400
87 |  | 9.3.5 | GR | Reactive Power Control, Normal Power Direction | Umax Control |  | 400
88 | Test Block-LP7 | 10.3.1 | GR/MR | Ground/Metallic Return Transfer | Ground/Metallic Return Transfer | Day5 | 200
89 |  | 10.3.2 | GR/MR | Ground/Metallic Return Transfer | Metallic Return Operation With Station Ground at LAHORE Converter Station |  | 200
90 | Test Block-LP8 | 15.3.1 | GR | Backup Control | Monopole Start/Stop in Backup Panel |  | 200
91 |  | 15.3.2 | GR | Backup Control | Monopole Ramp up/down in Backup Panel |  | 400
DC Monopolar Low Power Tests -Reverse Power
All DC Low Power Tests in Normal Direction must be successful before starting these tests
All tests in Test Block-LP9, LP10, LP11 should be executed in sequence as listed below. If any test fails in one block, next test item in the same block should not be executed however, next test block (Test Block- LP10,LP11) can be executed in the prescribed sequence.
92 | Test Block-LP9 | 11.3.1 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Start/Stop Pole | Day5 | 200
93 |  | 11.3.2 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Control System Switchover |  | 200
94 |  | 11.3.3 | GR/MR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Ground/Metallic Return Transfer |  | 200
95 |  | 12.3.1 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Start/Stop Pole, Joint Power Control |  | 200
96 |  | 12.3.2 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Control System Switchover |  | 200
DC Monopolar Low Power Disturbance Tests
All tests above must be sucessful before executing these tests
97 | Test Block-LP10 | 14.3.1 | GR | Disturbances | DC Filter Switching | Day6 | 200
98 |  | 14.3.2 | GR | Disturbances | Loss of 125V DC System C of Pole |  | 200
99 |  | 14.3.3 | GR | Disturbances | Loss of 125V DC System A of Pole |  | 300
100 |  | 14.3.4 | GR | Disturbances | Loss of 125V DC System B of Pole |  | 300
101 |  | 14.3.5 | GR | Disturbances | Simulated DC Line Fault (only Matiari) |  | 200
102 |  | 14.3.6 | GR | Disturbances | Simulate Fault of Converter Transformer PT Breaking at Matiari station |  | 200
103 |  | 14.3.7 | GR | Disturbances | Simulate Fault of Converter Transformer PT Breaking at LAHORE station |  | 200
104 |  | 14.3.8 | GR | Disturbances | Simulate Fault of DC Line PT Breaking at Matiari station |  | 200
105 |  | 14.3.9 | GR | Disturbances | Simulate Fault of DC Line PT Breaking at LAHORE station |  | 200
106 |  | 14.3.10 | GR | Disturbances | Simulate ACTIVE signal loss of pole control changeover device |  | 200
107 | Test Block-LP-11 | 13.3.1 | GR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Inverter in Ground Return |  | 200
108 |  | 13.3.3 | GR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Rectifier in Ground Return |  | 200
109 |  | 13.3.2 | MR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Inverter in Metallic Return |  | 200
110 |  |  | MR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Rectifier in Metallic Return |  | 200
Pole2 Low Power System Test (Protective Trip/Operational/Reverse Power/Disturbance)
Repeat Tests from Test No 55 to test No.110 for Pole-2
P2- 111-166 | LP3- LP-11 |  |  |  |  | Day 7-10
Bipole Low Power System Test
All tests above must be sucessful before executing these tests
All tests in LP 12,13,14,15 should be performed in sequence. May not proceed with suceeding tests within the block other than ramping tests if any test in the block fails. May not proceed with following block tests until each test block is complete.
Bipole Low Power Operational Tests
167 | LP-12 | 2.3.1 | BPGR | Initial Operation Tests, Normal Power Direction | Start/Stop Pole, Manual Deblock/Block | Day11 | 400
168 |  | 3.3.1 | BPGR | Pole Compensation | Normal Power Direction, Bipolar Power Ramping |  | 800
169 |  | 3.3.2 | BPGR | Pole Compensation | Normal Power Direction, Bipole Operation, Pole 2 Power Ramping |  | 800
170 |  | 3.3.3 | BPGR | Pole Compensation | Normal Power Direction, Bipole Operation, Pole 1 Power Ramping |  | 800
171 |  | 7.3.1 | BPGR | Automatic Power Curve Control Test | Automatic Power Curve Control test in Matiari Converter Station |  | 600
172 |  | 7.3.2 | BPGR | Automatic Power Curve Control Test | Automatic Power Curve Control test in Lahore Converter Station |  | 600
173 |  | 5.3.1 | BPGR | Reduced Voltage Operation | Reduced Voltage Operation Test |  | 600
174 |  | 9.3.1 | BPGR | Backup Control | Bipole Start/Stop in Backup Panel at Matiari |  | 400
175 |  | 9.3.1 | BPGR | Backup Control | Bipole Start/Stop in Backup Panel at Lahore |  | 400
176 |  | 9.3.2 | BPGR | Backup Control | Bipole Ramp up/down in Backup Panel |  | 600
Bipole Low Power Disturbance Tests
177 | LP-13 | 3.3.4 | BPGR | Pole Compensation by disturbance | Pole-2 Trip, Power Transfer at Normal Voltage |  | 800
178 |  | 3.3.4 | BPGR | Pole Compensation by disturbance | Pole-1 Trip, Power Transfer at Normal Voltage |  | 800
179 |  | 3.3.5 | BPGR | Pole Compensation by disturbance | Pole-1 Trip, Power Transfer at Reduced Voltage |  | 800
180 |  | 3.3.5 | BPGR | Pole Compensation by disturbance | Pole-2 Trip, Power Transfer at Reduced Voltage |  | 800
181 |  | 4.3.1 | BPGR | Operation with Station Ground | Start/Stop Bipole with Station Grounding at Matiari & LAHORE Converter Station |  | 600
182 |  | 6.3.1 | BPGR | Disturbances | Pole Trip, Open Line Fault at Electrode at Lahore | Day 11 | 400
183 |  | 6.3.1 | BPGR | Disturbances | Pole Trip, Open Line Fault at Electrode at Matiari |  | 400
184 |  | 6.3.2 | BPGR | Disturbances | Pole-1 in Operation while Pole-2 Undergoing Open Line Test |  | 400
185 |  | 6.3.2 | BPGR | Disturbances | Pole-2 in Operation while Pole-1 Undergoing Open Line Test |  | 400
186 |  | 6.3.3 | BPGR | Disturbances | Bipole Operation, Simulate Electrode Line Unbalance Fault |  | 600
187 |  | 6.3.4 | BPGR | Disturbances | Simulation of IDNC CT Transmitter Power Source Fault |  | 400
188 |  | 6.3.5 | BPGR | Disturbances | AC Auxiliary Power 400 V Switchover |  | 400
189 |  | 8.3.1 | BPGR | Frequency Control Test | Frequency Control test in Matiari Converter Station |  | 500
190 |  | 8.3.2 | BPGR | Frequency Control Test | Frequency Control test in Lahore Converter Station |  | 500
Bipole Low Power Tests -Reverse Power Direction
191 | LP-14 | 10.3.1 | BPGR | Initial Operation Tests, Reversed Power Direction | Start/Stop Bipole | Day 12 | 400
192 |  | 10.3.2 | BPGR | Initial Operation Tests, Reversed Power Direction | Control System Switchover |  | 400
193 |  | 11.3.1 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip X in Rectifier with Telecommunication |  | 400
194 |  | 11.3.2 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip Y in Inverter with Telecommunication |  | 400
195 |  | 11.3.3 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip Z in Rectifier with Telecommunication |  | 400
196 |  | 12.3.1 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Power Ramping |  | 800
197 |  | 12.3.2 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Operation, Pole 2 Power Ramping with/without Telecommunication |  | 600
198 |  | 12.3.2 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Operation, Pole 1 Power Ramping with/without Telecommunication |  | 600
199 |  | 12.3.3 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Simulated Pole1 DC Line Fault (only Lahore) |  | 400
200 |  | 12.3.4 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Simulated Pole2 DC Line Fault (only Lahore) |  | 400
Bipole Low Power Tests -AC and DC Line Fault Tests
201 | LP-15 | 13.3.1 | BPGR | DC Line Faults | DC Line Faults at Pole 1 near Rectifier, Normal Power Direction |  | 400
202 |  | 13.3.2 | BPGR | DC Line Faults | Pole 2 Reduced Voltage, DC Line Faults at Pole 2 near Rectifier, Normal Power Direction |  | 400
203 |  | 13.3.3 | BPGR | DC Line Faults | DC Line Faults at Pole 1 near Inverter, Normal Power Direction |  | 400
204 |  | 13.3.4 | BPGR | DC Line Faults | Pole 1 Reduced Voltage, DC Line Faults at Pole 1 near Inverter, Normal Power Direction | Day13 | 400
205 |  | 13.3.5 | BPGR | DC Line Faults | Pole 1 Reduced Voltage, DC Line Faults at Pole 2 near Inverter, Normal Power Direction |  | 400
206 |  | 13.3.6 | MR | DC Line Faults | DC Line Faults at Pole 2 near Inverter, Metallic Return Operation, Normal Power Direction |  | 200
207 |  | 13.3.4 | BPGR | DC Line Faults | Fault in Pole 2 at connection, with Pole-1 running at 200 MW |  | 400
208 |  | 13.3.5 | BPGR | DC Line Faults | DC Line Faults at Pole 1 near Rectifier, Reverse Power Direction |  | 400
209 |  | 13.3.6 | BPGR | DC Line Faults | DC Line Faults at Pole 2 near Inverter, Reverse Power Direction |  | 400
210 |  | 13.3.7 | BPGR | AC Line Faults | AC Line Faults at Rectifier, Normal Power Direction (Optional) |  | 400
211 |  | 13.3.8 | BPGR | AC Line Faults | AC Line Faults at Inverter, Normal Power Direction (Optional) |  | 400
High Power System Tests-Monpolar and Bipolar
All tests above must be sucessful before executing the High Power tests
The tests in HP1-HP-5 should be performed in sequence. In the case of any failure or delay in Block HP-1, next test in the block should not proceed until the reason for delay is resolved. However testing may proceed in HP-2 as long as the issue is not also common to HP-2. Similarly for a failure/delay in HP-3 testing should not proceed with next test in HP-3 but tests in HP-4 may proceed if the failure is not common to HP-3 and HP-4.
Pole1 High Power Tests, Normal Power Direction
212 | HP-1 | 2.3.1 | GR | Pole 1 High Power Test, | Pole Start | Day14 | 200
213 |  | 2.3.2 | BPGR | Pole 1 High Power Test | Power Ramp |  | 200-2000
214 |  | 2.3.3 | GR | Pole 1 High Power Test | Tap Changer Control, Manual Tap Changer Step |  | 2000
215 |  | 2.3.4 | GR /MR | Pole 1 High Power Test | Ground/Metallic Return Transfer |  | 2000
216 |  | 3.3.1 | GR | Pole 1 Heat Run Test and Special Measurements | Pole 1 Run at 1.00 p.u. in Monopole without Redundant Cooling |  | 2000
217 |  | 3.3.2 | GR | Pole 1 Heat Run Test and Special Measurements | Pole 1 Run at 1.1 p.u. in Monopole with Redundant Cooling |  | 2200
218 |  | 3.3.3 | GR | Pole 1 Heat Run Test and Special Measurements | Radio Interference Measurements |  | 2000/2200
219 |  | 3.3.4 | GR | Pole 1 Heat Run Test and Special Measurements | Audible Noise Check |  | 2000/2200
220 |  | 3.3.5 | GR | Pole 1 Heat Run Test and Special Measurements | Station Service Power Losses |  | 2000/2200
221 |  | 3.3.6 | GR | Pole 1 Heat Run Test and Special Measurements | Temperature Measurement With IR-Camera Equipment |  | 2000/2200
222 |  | 3.3.7 | GR | Pole 1 Heat Run Test and Special Measurements | Ground Electrode Test Program |  | 2000/2200
Pole2 High Power Tests, Normal Power Direction
223 | HP-2 | 4.3.1 | MR | Pole 2 High Power Test, | Pole Start | Day15 | 200
224 |  | 4.3.2 | MR | Pole 2 High Power Test | Power Ramp |  | 200-2000
225 |  | 4.3.3 | MR | Pole 2 High Power Test | Tap Changer Control, Manual Tap Changer Step |  | 2000
226 |  | 5.3.1 | MR | Pole 2 Heat Run Test and Special Measurements | Pole 2 Run at 1.00 p.u. in Monopole without Redundant Cooling |  | 2000
227 |  | 5.3.2 | MR | Pole 2 Heat Run Test and Special Measurements | Pole 2 Run at 1.1 p.u. in Monopole with Redundant Cooling |  | 2200
228 |  | 5.3.3 | MR | Pole 2 Heat Run Test and Special Measurements | Radio Interference Measurements |  | 2000/2200
229 |  | 5.3.4 | MR | Pole 2 Heat Run Test and Special Measurements | Audible Noise Check |  | 2000/2200
230 |  | 5.3.5 | MR | Pole 2 Heat Run Test and Special Measurements | Station Service Power Losses |  | 2000/2200
231 |  | 5.3.6 | MR | Pole 2Heat Run Test and Special Measurements | Temperature Measurement With IR-Camera Equipment |  | 2000/2200
232
Pole and Bipole High Power Test, Reversed Power Direction
233 | HP-3 | 6.3.1 | GR | Pole1 High Power Test | Pole Start | Day16 | 200
234 |  | 6.3.2 | GR | Pole1 High Power Test | Power Ramp (0.5pu) |  | 1000
235 |  | 3.3.1 | BPGR | Bipole High Power Operation | Bipole Power Ramping (0.5pu) |  | 2000
Bipole Rated Load Operation, Normal Power Direction
236 | HP-4 | 2.3.1 | BPGR | Bipole Rated Load Operation | Bipole Power Ramping | Day17 | 400-4000
237 |  | 2.3.2 | BPGR | Bipole Rated Load Operation | Heat Run Test at 1.00 p.u. |  | 4000
238 |  | 2.3.3 | BPGR | Bipole Rated Load Operation | Radio Interference Measurements |  | 4000
239 |  | 2.3.4 | BPGR | Bipole Rated Load Operation | Audible Noise Check |  | 4000
240 |  | 2.3.5 | BPGR | Bipole Rated Load Operation | Station Service Power Losses |  | 4000
241 |  | 2.3.6 | BPGR | Bipole Rated Load Operation | Temperature Measurement With IR-Camera Equipment |  | 4000