## 每日
拉合尔极Ⅰ换流站换流变温度、油位跟踪记录表（PoleⅠ Transformer TEMP And Oil Level Record）
项目Content 日期（Date） | 极ⅠY/Y换流变TFY-P1 A相 |  |  |  | 极ⅠY/Y换流变TFY-P1 B相 |  |  |  | 极ⅠY/Y换流变TFY-P1 C相 |  |  |  | 极ⅠY/Y换流变TFD-P1 A相 |  |  |  | 极ⅠY/Y换流变TFD-P1 B相 |  |  |  | 极ⅠY/Y换流变TFD-P1 C相 |  |  |  | 660kV穿墙套管压力（bar） U1P Gas Pressure | 阀侧套管SF6压力（kPA） Valve Casing Gas Pressure | [11 empty] | 负荷/MW Load | 环境温度（℃） TEMP | 抄录人 Recorder | 日对比 Normal
| OWS工作站（℃） |  |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | 冷却器 投入组数 Cooler
| 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 |  | 后台 | TFY-P1 C相a | TFY-P1 C相b | TFY-P1 B相a | TFY-P1 B相b | TFY-P1 A相a | TFY-P1 A相b | TFD-P1 A相a | TFD-P1 A相b | TFD-P1 B相a | TFD-P1 B相b | TFD-P1 C相a | TFD-P1 C相b
2020.08.01
2020.11.27 | [24 empty] | 0.602 | 0.357 | 0.359 | 0.36 | 0.362 | 0.342 | 0.327 | 0.363 | 0.366 | 0.358 | 0.352 | 0.345 | 0.352 | 0 | 0 | 战忠洋 | 正常
2020.12.04 | [24 empty] | 0.6 | 0.354 | 0.356 | 0.357 | 0.359 | 0.339 | 0.324 | 0.36 | 0.363 | 0.356 | 0.351 | 0.342 | 0.35 |  |  | 郭庆帅 | 正常
2020.12.12 | [24 empty] | 0.6 | 0.34 | 0.34 | 0.33 | 0.34 | 0.32 | 0.32 | 0.37 | 0.37 | 0.35 | 0.36 | 0.35 | 0.35 | 0 | 0 | 肖喜鹏 | 正常
2020.12.18 | [24 empty] | 0.596 | 0.36 | 0.36 | 0.34 | 0.34 | 0.32 | 0.31 | 0.37 | 0.37 | 0.36 | 0.36 | 0.35 | 0.36 | 0 | 0 | 肖喜鹏 | 正常
2020.12.25 | 10.4 | 11 | 10.8 | 0 | 11.2 | 11.4 | 11.2 | 0 | 11 | 11 | 11.4 | 0 | 11.2 | 11.3 | 11.1 | 0 | 11.3 | 11.1 | 11.2 | 0 | 11.1 | 11 | 11.4 | 0 | 6.05 | 346 | 345 | 345 | 340 | 320 | 312 | 370 | 375 | 365 | 355 | 355 | 360 | 0 | 19.5 | 王腾 | 正常

## 每周
拉合尔极Ⅰ换流站换流变温度、油位跟踪记录表（PoleⅠ Transformer TEMP And Oil Level Record）
项目Content 日期（Date） | 极ⅠY/Y换流变TFY-P1 A相 | [11 empty] | 极ⅠY/Y换流变TFY-P1 B相 | [11 empty] | 极ⅠY/Y换流变TFY-P1 C相 | [11 empty] | 极ⅠY/D换流变TFD-P1 A相 | [11 empty] | 极ⅠY/D换流变TFD-P1 B相 | [11 empty] | 极ⅠY/D换流变TFD-P1 C相 | [11 empty] | 660kV穿墙套管压力（bar） U1P Gas Pressure | 阀侧套管SF6压力（kPA） Valve Casing Gas Pressure | [11 empty] | 负荷/MW Load | 环境温度（℃） TEMP | 抄录人 Recorder | 日对比 Normal
| OWS工作站（℃） |  |  | PLC柜（℃） |  |  | 现场表计Meter（℃） |  |  | 油位（%）Oil Level |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | PLC柜（℃） |  |  | 现场表计Meter（℃） |  |  | 油位（%）Oil Level |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | PLC柜（℃） |  |  | 现场表计Meter（℃） |  |  | 油位（%）Oil Level |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | PLC柜（℃） |  |  | 现场表计Meter（℃） |  |  | 油位（%）Oil Level |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | PLC柜（℃） |  |  | 现场表计Meter（℃） |  |  | 油位（%）Oil Level |  | 冷却器 投入组数 Cooler | OWS工作站（℃） |  |  | PLC柜（℃） |  |  | 现场表计Meter（℃） |  |  | 油位（%）Oil Level |  | 冷却器 投入组数 Cooler
| 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 本体 Noumenon | 有载 Tap Switch |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 本体 Noumenon | 有载 Tap Switch |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 本体 Noumenon | 有载 Tap Switch |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 本体 Noumenon | 有载 Tap Switch |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 本体 Noumenon | 有载 Tap Switch |  | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 绕温 Wingding | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 底部油温 BOTTOM Oil | 顶部油温1 TOP Oil 1 | 顶部油温2 TOP Oil 2 | 本体 Noumenon | 有载 Tap Switch |  | 一体化数据 | TFY-P1 A相a | TFY-P1 A相b | TFY-P1 B相a | TFY-P1 B相b | TFY-P1 C相a | TFY-P1 C相b | TFD-P1 A相a | TFD-P1 A相b | TFD-P1 B相a | TFD-P1 B相b | TFD-P1 C相a | TFD-P1 C相b
2020.12.25 | 10.4 | 11 | 10.8 | 10.43 | 10.98 | 10.75 | 9.5 | 9.8 | 10 | 25 | 42 | 0 | 11.2 | 11.4 | 11.2 | 10 | 11.37 | 11.5 | 11 | 11 | 9 | 26 | 41 | 0 | 11 | 11 | 11.4 | 10 | 11.5 | 11.5 | 10 | 10 | 10 | 39 | 35.5 | 0 | 11.2 | 11.3 | 11.1 | 11.17 | 11.33 | 11.18 | 10 | 10 | 10 | 48.5 | 45.7 | 0 | 11.3 | 11.1 | 11.2 | 11.37 | 11.18 | 11.25 | 11 | 11 | 9.9 | 43 | 47.5 | 0 | 11.1 | 11 | 11.4 | 11.41 | 11.29 | 11.41 | 10 | 10 | 9 | 45.5 | 42.1 | 0 | 6.05 | 346 | 345 | 345 | 340 | 320 | 312 | 370 | 375 | 365 | 350 | 355 | 360 | 0 | 19.5
2021.1.1 | 11.6 | 12.2 | 12.1 | 8.09 | 8.6 | 8.71 | 8 | 6 | 8 | 20.1 | 39.8 | 0 | 12 | 12 | 11.9 | 8.52 | 9.03 | 8.79 | 8 | 6 | 6 | 19.7 | 40.3 | 0 | 11.2 | 11.4 | 11.7 | 8.4 | 8.87 | 8.52 | 8 | 6 | 8 | 36.9 | 34.2 | 0 | 12 | 12.1 | 11.4 | 8.56 | 8.4 | 9.03 | 7 | 6 | 8 | 47 | 45.6 | 0 | 12.3 | 12.2 | 11.8 | 8.56 | 8.73 | 9.07 | 9 | 8 | 8 | 46.6 | 41.8 | 0 | 12.4 | 12.5 | 11.9 | 8.44 | 8.56 | 8.91 | 7 | 5 | 6 | 45.1 | 40.7 | 0 | 0.593 | 0.33 | 0.34 | 0.33 | 0.34 | 0.32 | 0.31 | 0.37 | 0.375 | 0.37 | 0.35 | 0.35 | 0.36 | 0 | 16 | 钟永林 | 正常
2021.01.15 | 8.7 | 9.1 | 8.9 | 8.67 | 9.11 | 9.22 | 8 | 7 | 8 | 20.9 | 39.5 | 0 | 9 | 9.2 | 9.3 | 9.1 | 9.14 | 9.3 | 8 | 7 | 7 | 20.8 | 40.3 | 0 | 8.9 | 8.8 | 9.1 | 8.99 | 8.79 | 9.14 | 8 | 8 | 7 | 37.6 | 34 | 0 | 9.1 | 9.4 | 8.9 | 9.1 | 9.3 | 8.99 | 8 | 9 | 9 | 47.9 | 45.6 | 0 | 9.1 | 9 | 9 | 9.06 | 9.03 | 9.11 | 9 | 8 | 8 | 42.3 | 46.9 | 0 | 9 | 9.1 | 9.1 | 9.38 | 9.07 | 9.18 | 8 | 6 | 7 | 45.6 | 40.7 | 0 | 0.604 | 0.376 | 0.378 | 0.379 | 0.381 | 0.356 | 0.337 | 0.383 | 0.385 | 0.378 | 0.371 | 0.363 | 0.37 | 0 | 16 | Abdullah & Mani | 正常
2021.01.22 | 10.2 | 10.6 | 10.7 | 10.12 | 10.98 | 11.18 | 10 | 10 | 10 | 21.4 | 40.5 | 0 | 10.4 | 10.7 | 10.9 | 10.9 | 11.02 | 11.25 | 10 | 8 | 9 | 22 | 41 | 0 | 10.4 | 10.4 | 10.5 | 10.43 | 10.67 | 10.98 | 10 | 8 | 10 | 36.8 | 34.7 | 0 | 10.4 | 10.9 | 10.8 | 10.78 | 11.25 | 11.14 | 10 | 8.5 | 10 | 46.7 | 45.2 | 0 | 10.9 | 10.9 | 11.1 | 10.86 | 11.18 | 11.57 | 10.5 | 10 | 10 | 41.5 | 47.9 | 0 | 10.7 | 10.6 | 11.1 | 10.82 | 11.02 | 11.37 | 10 | 8.5 | 9 | 45.2 | 41.1 | 0 | 0.603 | 0.32 | 0.31 | 0.34 | 0.34 | 0.34 | 0.34 | 0.37 | 0.375 | 0.365 | 0.36 | 0.35 | 0.36 | 0 | 11.5 | Ahmad Usman | 正常
2021.01.29 | 11.7 | 12.2 | 14.5 | 10.7 | 11.4 | 11.5 | 10 | 10 | 11 | 24.5 | 41 | 0 | 11.9 | 12.4 | 13 | 11.17 | 11.37 | 11.53 | 10.5 | 10 | 10 | 25.1 | 41.5 | 0 | 11.6 | 11.8 | 12.9 | 11.02 | 11.02 | 11.37 | 10 | 9.5 | 10 | 37.8 | 34.8 | 0 | 12 | 12.5 | 12.1 | 10.86 | 11.25 | 11.14 | 10 | 9 | 10 | 47 | 45.5 | 0 | 12.5 | 12.3 | 12.4 | 11.29 | 11.18 | 11.57 | 11 | 10 | 10 | 41.5 | 48.4 | 0 | 12.7 | 12.9 | 12.8 | 11.41 | 11.29 | 11.64 | 10.2 | 9 | 10 | 41.5 | 41.5 | 0 | 0.597 | 0.33 | 0.34 | 0.33 | 0.34 | 0.31 | 0.32 | 0.37 | 0.375 | 0.365 | 0.36 | 0.355 | 0.36 | 0 | 12 | Habib Ullah & Abdullah | 正常
2021.02.05 | 13.1 | 13.8 | 14.5 | 13.44 | 14.3 | 15.9 | 10.1 | 10.2 | 10.8 | 27.5 | 40.8 | 0 | 13.7 | 13.7 | 13.9 | 14.06 | 14.03 | 14.81 | 10.5 | 10.1 | 10.2 | 28.4 | 41.4 | 0 | 13.6 | 13.3 | 13.8 | 13.83 | 13.56 | 14.69 | 10.3 | 10 | 10.4 | 26.2 | 35.2 | 0 | 13.9 | 13.9 | 13.9 | 13.87 | 14.22 | 14.46 | 10.2 | 10.2 | 10.5 | 27 | 44.6 | 0 | 13.9 | 13.5 | 14 | 14.18 | 13.99 | 14.54 | 10.5 | 10.2 | 10.5 | 29.9 | 48.7 | 0 | 13.9 | 13.9 | 13.9 | 14.22 | 14.26 | 14.54 | 10.1 | 10 | 10.02 | 26.1 | 41.7 | 0 | 0.599 | 0.345 | 0.345 | 0.34 | 0.34 | 0.31 | 0.33 | 0.375 | 0.37 | 0.368 | 0.37 | 0.36 | 0.355 | 0 | 13.79 | Ahmad Usman | 正常
2021.02.12 | 15.2 | 16.1 | 17.8 | 14.3 | 15.16 | 16.8 | 14 | 14 | 17 | 27.5 | 40.9 | 0 | 15.3 | 15.2 | 17.6 | 14.88 | 15.88 | 16.45 | 14 | 13 | 15 | 28.5 | 41.1 | 0 | 15 | 15 | 17.4 | 14.73 | 14.5 | 16.49 | 14 | 13 | 15 | 26.2 | 35.4 | 0 | 16 | 16.3 | 15.5 | 15.04 | 15.12 | 15 | 14 | 14 | 14 | 35.1 | 44.7 | 0 | 16.4 | 16.1 | 15.7 | 15.04 | 14.85 | 15.2 | 15 | 14 | 14 | 30.3 | 46 | 0 | 16.2 | 16.2 | 15.7 | 15.08 | 15.08 | 15.12 | 14 | 14 | 14 | 26.1 | 42.1 | 0 | 0.586 | 0.34 | 0.345 | 0.34 | 0.34 | 0.32 | 0.31 | 0.37 | 0.37 | 0.36 | 0.36 | 0.36 | 0.35 | 0 | 26 | Abdullah & Habib Ullah | 正常
2021.02.19 | 14.9 | 15.4 | 15.3 | 14.3 | 14.89 | 14.73 | 14 | 14 | 14 | 29.4 | 41.7 | 0 | 15.2 | 15.2 | 15.4 | 14.88 | 14.89 | 15.08 | 14.5 | 12.5 | 12.5 | 29.6 | 42 | 0 | 15 | 15 | 15.2 | 15 | 14.73 | 14.65 | 14.1 | 12 | 14 | 27.7 | 35.9 | 0 | 15 | 15.5 | 15 | 14.78 | 14.81 | 14.85 | 14.2 | 12.3 | 14 | 30.5 | 43.3 | 0 | 15.3 | 15.1 | 15.1 | 14.77 | 14.61 | 14.85 | 14.5 | 14 | 13 | 32.2 | 46.3 | 0 | 15.4 | 15.1 | 15.3 | 14.81 | 14.85 | 14.89 | 14 | 12 | 13 | 28.3 | 42.2 | 0 | 0.601 | 0.34 | 0.345 | 0.33 | 0.34 | 0.32 | 0.3 | 0.369 | 0.37 | 0.36 | 0.359 | 0.35 | 0.352 | 0 | 18.5 | Ahmad Usman | 正常
2021.02.26 | 21 | 21.5 | 22.8 | 20.35 | 20.94 | 21.06 | 20 | 20 | 20 | 33.5 | 43.5 | 0 | 21.2 | 21.1 | 22.3 | 20.74 | 20.63 | 21.06 | 20 | 20 | 20 | 34.5 | 43 | 0 | 20.7 | 20.8 | 22.5 | 20.19 | 20.16 | 20.83 | 20 | 20 | 20 | 30.1 | 37.2 | 0 | 21.1 | 21.5 | 21.7 | 20.82 | 20.73 | 21.06 | 20 | 20 | 20.5 | 31.8 | 43.7 | 0 | 21.1 | 21.2 | 21.8 | 20.67 | 20.5 | 21.29 | 20 | 20 | 20 | 35.9 | 45.5 | 0 | 21.3 | 21.2 | 21.9 | 21.14 | 20.79 | 21.06 | 20 | 20 | 20 | 29.7 | 41.7 | 0 | 0.592 | 0.33 | 0.34 | 0.34 | 0.34 | 0.32 | 0.3 | 0.36 | 0.37 | 0.36 | 0.36 | 0.34 | 0.35 | 0 | 18 | Qasim | 正常
2021.03.05 | 27.3 | 28.3 | 28.8 | 27.3 | 28.3 | 28.8 | 28 | 28 | 28 | 39.1 | 45 | 0 | 27.5 | 27.4 | 29.3 | 27.5 | 27.4 | 29.3 | 26 | 28 | 28 | 39.4 | 49.1 | 0 | 27.6 | 27.4 | 29.6 | 27.6 | 27.4 | 29.6 | 26 | 26 | 28 | 35.1 | 38.5 | 0 | 27.1 | 27.5 | 26.8 | 27.1 | 27.5 | 26.8 | 26 | 26 | 26 | 35.8 | 46.9 | 0 | 27.6 | 27.1 | 27.4 | 27.6 | 27.1 | 27.4 | 26 | 26 | 25 | 40.3 | 45.9 | 0 | 27.5 | 27.1 | 27 | 27.5 | 27.1 | 27 | 25 | 24 | 25 | 34.7 | 44.9 | 0 | 0.591 | 0.36 | 0.34 | 0.34 | 0.34 | 0.32 | 0.3 | 0.36 | 0.365 | 0.36 | 0.36 | 0.34 | 0.35 | 0 | 23 | Zubair Tufail | 正常
2021.03.14 | 33.9 | 34.6 | 34 | 31.29 | 32.31 | 32.31 | 32 | 32 | 32 | 40.4 | 46.5 | 0 | 34.6 | 34.5 | 34.4 | 32.31 | 31.96 | 32.39 | 32 | 31 | 32 | 41.8 | 43.1 | 0 | 33.7 | 34.1 | 34.1 | 31.68 | 31.37 | 32.15 | 31 | 30 | 32 | 37.1 | 39.7 | 0 | 34.2 | 34.6 | 32.7 | 31.49 | 31.76 | 31.8 | 32 | 31 | 31 | 36.5 | 45 | 0 | 34.3 | 33.9 | 32.8 | 31.25 | 31.41 | 31.73 | 32 | 31 | 31 | 43.5 | 45.6 | 0 | 34.4 | 34.2 | 32.7 | 31.57 | 31.14 | 31.53 | 31 | 31 | 31 | 35.5 | 45.7 | 0 | 0.591 | 0.33 | 0.345 | 0.33 | 0.345 | 0.31 | 0.3 | 0.355 | 0.348 | 0.334 | 0.35 | 0.34 | 0.35 | 0 | 22 | Abdullah Rashid | 正常
2021.03.19 | 27.9 | 28.5 | 28.9 | 28.3 | 28.3 | 28.6 | 28 | 28 | 30 | 37.6 | 45 | 0 | 28.5 | 28.1 | 28.6 | 28.2 | 27.7 | 28.8 | 28 | 28 | 29 | 41.9 | 45.6 | 0 | 28.5 | 28.9 | 30 | 29.3 | 29.2 | 29.5 | 29 | 29 | 30 | 36.6 | 45.7 | 0 | 27.8 | 28.1 | 27.9 | 28.4 | 29.4 | 29.4 | 29 | 29 | 30 | 39.4 | 46 | 0 | 27.5 | 26.6 | 28.2 | 29.1 | 28.8 | 29.8 | 29 | 29 | 30 | 41 | 45.1 | 0 | 28.9 | 28.9 | 29.2 | 29.1 | 29.6 | 30.6 | 30 | 29 | 30.2 | 36.5 | 39.4 | 0 | 0.593 | 0.34 | 0.35 | 0.35 | 0.36 | 0.35 | 0.3 | 0.33 | 0.35 | 0.34 | 0.347 | 0.34 | 0.345 | 0 | 24.6 | M.Ashraf | 正常
2021.03.26 | 34.5 | 34.8 | 36.1 | 32.46 | 33.4 | 34.66 | 34 | 34 | 36 | 36.8 | 43.4 | 1 | 35.5 | 34.7 | 36.7 | 33.29 | 33.05 | 35.1 | 34 | 34 | 37 | 43.4 | 38.8 | 1 | 33.4 | 32.8 | 36.7 | 30.32 | 30.2 | 36.06 | 32 | 32 | 36 | 33.7 | 37.7 | 1 | 33.3 | 33.4 | 34.7 | 30.75 | 31.76 | 33.52 | 30 | 32 | 35 | 34.2 | 44.7 | 1 | 33.5 | 33.6 | 34.6 | 31.21 | 31.8 | 33.48 | 32 | 32 | 34 | 40.4 | 45.3 | 1 | 33.2 | 33.3 | 34.7 | 30.7 | 31.14 | 33.29 | 32 | 32 | 34 | 33 | 44 | 1 | 0.591 | 0.35 | 0.35 | 0.34 | 0.35 | 0.33 | 0.3 | 0.36 | 0.37 | 0.36 | 0.36 | 0.34 | 0.35 | 0 | 24 | M.Ashraf | 正常
2021.04.02 | 38.2 | 38.29 | 39.03 | 37.27 | 37.4 | 38.7 | 39.5 | 39 | 40 | 41.8 | 45.9 | 1 | 39.97 | 38.48 | 40.16 | 40 | 39.4 | 39.4 | 39.11 | 39.5 | 39.5 | 42.7 | 44.8 | 1 | 38.91 | 38.29 | 41.14 | 38.64 | 37.19 | 41.02 | 40 | 39.5 | 41 | 38.2 | 40 | 1 | 37.58 | 37.12 | 37.35 | 36.5 | 35.6 | 36.84 | 38.5 | 38.5 | 39 | 39.5 | 44.8 | 1 | 38.05 | 36.68 | 37.04 | 36.9 | 35.5 | 36.4 | 38 | 39 | 38 | 42.9 | 45.5 | 1 | 37.54 | 36.21 | 37.23 | 36.29 | 35.01 | 36.6 | 38 | 37 | 39 | 37.5 | 45.4 | 1 | 0.592 | 0.34 | 0.34 | 0.34 | 0.35 | 0.32 | 0.29 | 0.36 | 0.36 | 0.35 | 0.36 | 0.34 | 0.35 | -390.7 | 22 | Ahmad Usman | 正常
2021.04.03 | 41.4 | 42.5 | 42.5 | 41.45 | 42.55 | 42.59 | 44 | 44 | 44 | 40.3 | 45.3 | 0 | 41.8 | 41.9 | 42.9 | 42.11 | 41.69 | 42.7 | 43 | 44 | 44 | 40.9 | 44 | 0 | 41.3 | 41.4 | 43.7 | 41.33 | 41.3 | 43.45 | 42 | 42 | 45 | 36.3 | 39.1 | 0 | 41.5 | 41.8 | 41.1 | 40.86 | 41.18 | 40.52 | 41 | 43 | 42 | 38.6 | 44.3 | 0 | 42.2 | 42 | 41.3 | 41.22 | 41.02 | 40.75 | 42 | 42 | 41 | 42 | 44.9 | 0 | 41.4 | 41.2 | 40.7 | 40.63 | 40.52 | 40.12 | 42 | 42 | 42 | 36.8 | 44.5 | 0 | 0.589 | 0.35 | 0.348 | 0.348 | 0.35 | 0.314 | 0.299 | 0.36 | 0.364 | 0.353 | 0.358 | 0.34 | 0.348 | 0 | 27 | Abdullah Rashid | 正常
2021.04.04 | 30.39 | 31.06 | 30.39 | [9 empty] | 30.47 | 30.71 | 32.11 | [9 empty] | 31.29 | 31.02 | 31.76 | [9 empty] | 30.19 | 30.94 | 31.33 | [9 empty] | 29.69 | 29.65 | 30.79 | [9 empty] | 29.92 | 29.96 | 30.43 | [10 empty] | 0.328 | 0.305 | 0.358 | 0.36 | 0.356 | 0.357 | 0.361 | 0.364 | 0.356 | 0.35 | 0.342 | 0.349 | 0 |  | M.Usman, Adeel | 正常
2021.04.05 | 27.77 | 28.48 | 28.4 | [9 empty] | 28.13 | 27.89 | 28.71 | [9 empty] | 28.4 | 28.52 | 28.36 | [9 empty] | 27.85 | 27.86 | 28.17 | [9 empty] | 28.44 | 28.25 | 27.62 | [9 empty] | 27.7 | 26.92 | 27.7 | [10 empty] | 0.356 | 0.358 | 0.365 | 0.361 | 0.354 | 0.355 | 0.36 | 0.362 | 0.355 | 0.35 | 0.341 | 0.349 | 0 |  | M.Usman, Adeel | 正常
2021.04.06 | 25.5 | 26.1 | 26 | [8 empty] | 0 | 26.1 | 25.9 | 26.3 | [8 empty] | 0 | 25.9 | 25.9 | 25.7 | [8 empty] | 0 | 25.1 | 25.5 | 25.4 | [8 empty] | 0 | 25.6 | 24.8 | 25.7 | [8 empty] | 0 | 25.7 | 25.7 | 25.5 | [8 empty] | 0 | 0.589 | 0.36 | 0.36 | 0.36 | 0.36 | 0.35 | 0.35 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.35 | 0 | 22.8 | Ahmad Usman | 正常
2021.04.07 | 23.05 | 23.63 | 25.32 | [9 empty] | 23.47 | 25.08 | 23.4 | [9 empty] | 23.05 | 23.28 | 25.08 | [9 empty] | 22.93 | 22.93 | 23.44 | [9 empty] | 22.89 | 23.17 | 23.28 | [9 empty] | 22.81 | 22.89 | 23.52 | [10 empty] | 0.364 | 0.366 | 0.372 | 0.369 | 0.361 | 0.362 | 0.367 | 0.37 | 0.363 | 0.358 | 0.349 | 0.357 |  |  | M.Usman, Adeel | 正常
2021.04.08 | 22.74 | 23.3 | 25.3 | [8 empty] | 0 | 23.21 | 23.09 | 25.3 | [8 empty] | 0 | 22.7 | 22.8 | 25.3 | [8 empty] | 0 | 22.62 | 22.9 | 24.18 | [8 empty] | 0 | 22.89 | 22.7 | 23.6 | [8 empty] | 0 | 22.8 | 22.8 | 23.5 | [8 empty] | 0 | 0.596 | 0.36 | 0.36 | 0.36 | 0.36 | 0.35 | 0.36 | 0.36 | 0.36 | 0.36 | 0.35 | 0.34 | 0.35 | 0 | 22 | Ahmad Usman | 正常
2021.04.09 | 23.8 | 24 | 26.9 | [8 empty] | 0 | 23.8 | 24.1 | 26.2 | [8 empty] | 0 | 23.6 | 23.6 | 26.4 | [8 empty] | 0 | 23.8 | 24.3 | 24.8 | [8 empty] | 0 | 24.2 | 23.4 | 24.9 | [8 empty] | 0 | 23.7 | 24 | 24.7 | [8 empty] | 0 | 0.588 | 0.35 | 0.35 | 0.35 | 0.35 | 0.36 | 0.36 | 0.36 | 0.36 | 0.35 | 0.35 | 0.34 | 0.35 | 0 | 22 | Abu Bakar | 正常
2021.04.10 | 23.7 | 24.3 | 26.6 | [8 empty] | 0 | 24.1 | 24.5 | 26.4 | [8 empty] | 0 | 26.6 | 25.1 | 27.4 | [8 empty] | 0 | 24.8 | 25.2 | 25.4 | [8 empty] | 0 | 24.7 | 23.7 | 25.2 | [8 empty] | 0 | 24.5 | 24.5 | 25 | [8 empty] | 0 | 0.582 | 0.36 | 0.36 | 0.35 | 35 | 0.35 | 0.35 | 0.36 | 0.36 | 0.35 | 0.35 | 0.34 | 0.34 | 0 | 25.3 | Ahmad Usman | 正常
2021.04.11 | 26.4 | 29 | 25.8 | [8 empty] | 0 | 26.4 | 28.7 | 26.9 | [8 empty] | 0 | 26.3 | 29.3 | 26.8 | [8 empty] | 0 | 26.8 | 26.5 | 26.8 | [8 empty] | 0 | 26.3 | 27 | 27.2 | [8 empty] | 0 | 26.8 | 27 | 27 | [8 empty] | 0 | 0.591 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.33 | 0.34 | 0 | 29.2 | Abdullah Rashid | 正常
2021.04.13 | 27 | 27.6 | 30.5 | [8 empty] | 0 | 28 | 27.6 | 30.3 | [8 empty] | 0 | 27.6 | 27.4 | 30.7 | [8 empty] | 0 | 28.1 | 28.4 | 27.7 | [8 empty] | 0 | 28.7 | 28.6 | 28.8 | [8 empty] | 0 | 28.1 | 28.4 | 28.4 | [8 empty] | 0 | 0.587 | 0.34 | 0.34 | 0.34 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.34 | 0 | 26 | M.Ashraf | 正常
2021.04.14 | 27.31 | 27.62 | 29.2 | [9 empty] | 27.7 | 27.6 | 29 | [9 empty] | 27.3 | 27.4 | 29 | [9 empty] | 27.4 | 27.7 | 27.5 | [9 empty] | 27.5 | 27.7 | 28.1 | [9 empty] | 27.5 | 27.4 | 27.9 | [10 empty] | 0.35 | 0.35 | 0.34 | 0.35 | 0.34 | 0.34 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.34 |  |  | Usman | 正常
2021.04.15 | 37.2 | 35.2 | 37 | [8 empty] | 1 | 36.8 | 36.2 | 38.1 | [8 empty] | 1 | 35.8 | 36.9 | 37 | [8 empty] | 1 | 35 | 35 | 36.2 | [8 empty] | 1 | 36 | 35.2 | 37.5 | [8 empty] | 1 | 35.3 | 35.4 | 36.5 | [8 empty] | 1 | 0.593 | 0.35 | 0.35 | 0.35 | 0.35 | 0.36 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.33 | -293.1 | 24 | Abdullah Rashid | 正常
2021.04.16 | 38.5 | 38.7 | 37.3 | 38.52 | 38.68 | 38.09 | 40 | 40 | 40 | 43.5 | 46.5 | 1 | 39.6 | 38.6 | 39.1 | 39.61 | 38.68 | 39.07 | 40 | 40 | 40 | 44.4 | 45.5 | 1 | 38.9 | 38 | 40 | 38.91 | 38.05 | 40.32 | 40 | 40 | 41 | 39.8 | 40.1 | 1 | 38.7 | 37.6 | 37.6 | 38.68 | 37.59 | 37.9 | 40 | 39 | 39 | 41 | 47.5 | 1 | 39.3 | 37.8 | 37.5 | 39.3 | 37.78 | 37.47 | 40 | 40 | 40 | 45.3 | 45.8 | 1 | 38.5 | 37.2 | 37.2 | 38.5 | 37.19 | 37.23 | 40 | 40 | 40 | 39.2 | 46.4 | 1 | 0.596 | 0.34 | 0.34 | 0.35 | 0.345 | 0.352 | 0.358 | 0.35 | 0.35 | 0.33 | 0.34 | 0.34 | 0.34 | -382.3 | 26 | M.Ashraf | 正常
2021.04.17 | 34.8 | 35.2 | 34.9 | 35.12 | 35.51 | 35.2 | 36 | 35 | 36 | 40.6 | 45.1 | 1 | 35 | 34 | 35.3 | 35.5 | 35.9 | 36.58 | 35 | 35 | 36 | 41.3 | 44.7 | 1 | 35.1 | 34.6 | 37.3 | 35.47 | 35 | 37.35 | 36 | 36 | 37 | 37.5 | 38.8 | 1 | 35.4 | 34.8 | 35 | 35.6 | 35.05 | 35.08 | 36 | 35 | 36 | 39.8 | 47.8 | 1 | 34.7 | 34.2 | 33.8 | 35.08 | 34.1 | 33.99 | 35 | 36 | 34 | 42.4 | 45.6 | 1 | 34.8 | 33.8 | 33.8 | 34.8 | 33.7 | 33.9 | 35 | 35 | 34.4 | 36.7 | 45.4 | 1 | 0.592 | 0.35 | 0.35 | 0.34 | 0.345 | 0.34 | 0.34 | 0.355 | 0.36 | 0.35 | 0.345 | 0.34 | 0.34 | -242.7 | 25 | Ahmad & Abdullah & Ashraf | 正常
2021.04.18 | 38.48 | 38.32 | 39.3 | [8 empty] | 1 | 38.75 | 37.19 | 40 | [8 empty] | 1 | 38.05 | 36.88 | 41.3 | [8 empty] | 1 | 39.42 | 38.56 | 38.48 | [8 empty] | 1 | 39.96 | 38.95 | 38.13 | [8 empty] | 1 | 39.42 | 38.75 | 38.09 | [8 empty] | 1 | 0.589 | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.33 | -293 | 33.4 | Ahmad Usman | 正常
2021.04.19 | 37.9 | 37.5 | 39.3 | [8 empty] | 1 | 36.8 | 39.7 | 38.7 | [8 empty] | 1 | 36.3 | 41 | 37.7 | [8 empty] | 1 | 35.9 | 35 | 36.5 | [8 empty] | 1 | 38.1 | 36.6 | 36.8 | [8 empty] | 1 | 37.6 | 36.2 | 37 | [8 empty] | 1 |  | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.34 | -391.1 | 27.7 | Ahmad Usman | 正常
2021.04.20 | 40.86 | 41.02 | 40.47 | [8 empty] | 1 | 41.45 | 40.2 | 41.17 | [8 empty] | 1 | 40.47 | 39.3 | 42.15 | [8 empty] | 1 | 42.35 | 40.86 | 40.24 | [8 empty] | 1 | 43.05 | 41.02 | 39.85 | [8 empty] | 1 | 42.38 | 40.52 | 39.85 | [8 empty] | 1 |  | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | -392.1 | 30.1 | Ahmad Usman | 正常
2021.04.21 | 33.48 | 33.47 | 33.95 | [8 empty] | 1 | 33.28 | 33.36 | 35.08 | [8 empty] | 1 | 34.81 | 34.97 | 35.71 | [8 empty] | 1 | 33.91 | 33.56 | 33.52 | [8 empty] | 1 | 34.21 | 33.17 | 33.6 | [8 empty] | 1 | 30.35 | 33.59 | 32.97 | [8 empty] | 1 | 0.591 | 0.36 | 0.36 | 0.35 | 0.35 | 0.35 | 0.37 | 0.36 | 0.36 | 0.34 | 0.35 | 0.34 | 0.34 | 195.6 | 30 | usman | 正常
2021.04.22 | 33.95 | 34.65 | 33.48 | [8 empty] | 1 | 34.69 | 34.3 | 34.14 | [8 empty] | 1 | 33.71 | 33.44 | 34.81 | [8 empty] | 1 | 33.83 | 33.52 | 33.25 | [8 empty] | 1 | 34.14 | 33.52 | 33.48 | [8 empty] | 1 | 33.91 | 33.52 | 33.56 | [8 empty] | 1 | 0.589 | 0.36 | 0.36 | 0.35 | 0.35 | 0.35 | 0.37 | 0.36 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 196.2 | 28 | Ashraf | 正常
2021.04.23 | 30.2 | 31.9 | 32.9 | 30.2 | 31.6 | 32 | 30.1 | 31.2 | 31 | 39 | 44 | 1 | 30.7 | 31.4 | 33.2 | 30.3 | 31 | 32.3 | 29.8 | 30.2 | 31 | 39.5 | 43 | 1 | 29.7 | 30.5 | 33.9 | 29.6 | 29.8 | 33 | 29.8 | 29.2 | 31 | 35 | 36 | 1 | 29.5 | 29.8 | 30.9 | 29.2 | 29.5 | 30.6 | 28 | 27.9 | 29.5 | 38 | 46 | 1 | 30.9 | 30.1 | 31.4 | 30.67 | 30.83 | 30.7 | 30.1 | 30 | 31 | 41 | 46 | 1 | 30.4 | 30.5 | 31.5 | 29.8 | 30.2 | 31.2 | 29 | 29 | 29.8 | 36 | 44 | 1 | 0.594 | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36 | 0.36 | 0.35 | 0.34 | 0.34 | 0.365 | 0 | 18 | Abdullah Rashid & Usman | 正常
2021.04.24 | 34.2 | 34.4 | 38.5 | 32.19 | 32.23 | 35.5 | 34 | 34 | 39 | 39.1 | 43.8 | 1 | 36.5 | 35.6 | 38.8 | 35 | 34 | 38.1 | 35 | 35 | 40 | 39.6 | 43 | 1 | 34 | 33.2 | 39.8 | 33.13 | 32.6 | 39.27 | 35 | 34 | 40 | 34.2 | 36.3 | 1 | 34.7 | 34.8 | 36.3 | 32.39 | 32.62 | 34.42 | 32 | 34 | 35 | 37.4 | 45.5 | 1 | 33.4 | 33.2 | 33.8 | 33.56 | 33.6 | 35.24 | 34 | 34.5 | 35 | 41.3 | 45.5 | 1 | 34 | 33.2 | 33.3 | 33.01 | 33.17 | 35.01 | 34 | 34 | 36 | 35.8 | 43.7 | 1 | 0.588 | 0.345 | 0.345 | 0.34 | 0.342 | 0.34 | 0.34 | 0.355 | 0.36 | 0.355 | 0.345 | 0.34 | 0.345 | 400 | 28.7 | Ahmad Usman | 正常
2021.04.25 | 37 | 37.8 | 39.8 | [8 empty] | 1 | 38.4 | 37.7 | 40.6 | [8 empty] | 1 | 37.7 | 37.1 | 42 | [8 empty] | 1 | 35.6 | 35.9 | 37.5 | [8 empty] | 1 | 36 | 36.6 | 38 | [8 empty] | 1 | 35.9 | 36.1 | 37.7 | [8 empty] | 1 | 0.589 | 0.35 | 0.35 | 0.34 | 0.35 | 0.34 | 0.34 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.34 | -193.4 | 35.4 | Usman | 正常
2021.04.26 | 37.6 | 37.4 | 39.8 | [8 empty] | 2 | 38.1 | 36.1 | 40.5 | [8 empty] | 2 | 37.7 | 35.5 | 41.3 | [8 empty] | 2 | 40 | 39.1 | 39.6 | [8 empty] | 2 | 40.5 | 38.9 | 39.6 | [8 empty] | 2 | 40 | 38.6 | 39.8 | [8 empty] | 2 | 0.59 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.32 | 0.33 | -392.3 | 32.3 | Usman | 正常
2021.04.27 | 39.26 | 38.68 | 40.47 |  |  |  | 44 | 42 | 45 | 45 | 45.5 | 2 | 39.92 | 37.77 | 41.37 |  |  |  | 42 | 41 | 46 | 45 | 44 | 2 | 39.22 | 37.19 | 42.15 |  |  |  | 42 | 42 | 46 | 40.5 | 38.9 | 2 | 38.48 | 38.17 | 39.64 |  |  |  | 38 | 42 | 44 | 50.1 | 54.6 | 2 | 39.37 | 38.36 | 39.89 |  |  |  | 42 | 43 | 44 | 36.7 | 47.9 | 2 | 39.42 | 38.4 | 39.84 |  |  |  | 42 | 42 | 44 | 42.4 | 46.4 | 2 | 0.58 | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.32 | 0.33 | 368 | 36.5 | Adeel & Ashraf | 正常
2021.04.28 | 46.68 | 46.6 | 47.7 | [8 empty] | 2 | 47.72 | 45.75 | 48.21 | [8 empty] | 2 | 46.76 | 45.71 | 49.3 | [8 empty] | 2 | 47.34 | 46.77 | 46.33 | [8 empty] | 2 | 47.42 | 46.37 | 46.92 | [8 empty] | 2 | 50.48 | 46.69 | 47.7 | [8 empty] | 2 | 0.582 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.32 | 0.32 | 0.32 | -380.7 | 40.2 | Ahmad Usman | 正常
2021.04.29 | 39.37 | 38.99 | 39.65 | [8 empty] | 2 | 40.59 | 38.95 | 40.52 | [8 empty] | 2 | 39.81 | 38.05 | 41.22 | [8 empty] | 2 | 39.03 | 37.85 | 39.65 | [8 empty] | 2 | 39.3 | 38.05 | 38.99 | [8 empty] | 2 | 39.69 | 38.4 | 39.03 | [8 empty] | 2 | 0.584 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | -381.7 | 31.2 | Abdullah & Abu Bakar | 正常
2021.04.30 | 43.4 | 43.1 | 46 | 41.3 | 39.8 | 43.87 | 41 | 41 | 42.5 | 40.4 | 39.1 | 2 | 44.9 | 42.8 | 47 | 41.7 | 40.12 | 42.92 | 41.5 | 41 | 42 | 45.5 | 45.3 | 2 | 44 | 42.7 | 47.6 | 40.86 | 40.4 | 41.92 | 41.5 | 41 | 42 | 46.2 | 46.6 | 2 | 43.5 | 43 | 44.6 | 40 | 39.34 | 40.91 | 40 | 41 | 40 | 41.8 | 47.9 | 2 | 44 | 43.2 | 44.6 | 40.51 | 40.44 | 39.58 | 40 | 41 | 40 | 46 | 45.5 | 2 | 44.3 | 43.3 | 44.7 | 40.63 | 39.27 | 40.71 | 40.63 | 40 | 41.2 | 40 | 46.2 | 2 | 0.58 | 0.35 | 0.35 | 0.345 | 0.34 | 0.335 | 0.34 | 0.35 | 0.35 | 0.34 | 0.345 | 33 | 0.33 | -380.5 | 36 | Abdullah Rashid | 正常
2021.05.01 | 42 | 40.4 | 42.6 | [9 empty] | 42 | 40.7 | 43.8 | [9 empty] | 41 | 39.5 | 44.6 | [9 empty] | 40.6 | 39.5 | 41 | [9 empty] | 41.1 | 40.1 | 41 | [9 empty] | 40.5 | 39.9 | 41.4 | [9 empty] | 0.59 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.32 | 0.33 | 382 | 32.5 | Kashif | 正常
2021.05.02 | 39.4 | 39.3 | 36.5 | [9 empty] | 39 | 39.7 | 37.1 | [9 empty] | 38 | 40 | 36.6 | [9 empty] | 37.6 | 36.5 | 37.8 | [9 empty] | 37.9 | 36.6 | 37.5 | [9 empty] | 37.9 | 36.9 | 37.8 | [9 empty] | 0.589 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.33 | 382 | 30 | Rehan | 正常
2021.05.03 | 38.6 | 37.4 | 40.8 | [8 empty] | 2 | 40.1 | 38.5 | 40.7 | [8 empty] | 2 | 39.1 | 38.9 | 39.9 | [8 empty] | 2 | 39 | 38.3 | 39.4 | [8 empty] | 2 | 38.9 | 39 | 37.8 | [8 empty] | 2 | 39 | 38.1 | 38.9 | [8 empty] | 2 | 0.59 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.35 | 0.34 | 0.34 | 0.35 | 0.33 | 0.33 | -380 | 30.3 | Ahmad Usman | 正常
2021.05.04 | 42.5 | 43.6 | 42.7 | [9 empty] | 42 | 44.8 | 43.6 | [9 empty] | 41.1 | 45.3 | 42.4 | [9 empty] | 42 | 42.9 | 42.6 | [9 empty] | 41.8 | 42.5 | 42.5 | [9 empty] | 42 | 42.9 | 42.7 | [9 empty] | 0.587 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.34 | 0.35 | 0.34 | 0.35 | 0.33 | 0.33 | -341 | 35 | Abdullah Rashid | 正常
2021.05.05
2021.05.05 | 38.2 | 38 | 38.7 | [9 empty] | 37.4 | 36.1 | 39.1 | [9 empty] | 37 | 35.8 | 40 | [9 empty] | 38.2 | 37.3 | 37.6 | [9 empty] | 38.5 | 37.3 | 37.5 | [9 empty] | 38.8 | 37.8 | 37.8 | [9 empty] | 0.59 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.35 | 0.34 | 0.33 | 0.33 | 0.33 | 391 | 29.6 | Adeel & Ashraf | 正常
2021.05.06 | 37.62 | 37.74 | 38.13 | [9 empty] | 41.76 | 40.17 | 41.17 | [9 empty] | 40.98 | 40.47 | 42.27 | [9 empty] | 40.2 | 39.61 | 39.92 | [9 empty] | 41.99 | 40.67 | 40.16 | [9 empty] | 41.45 | 40.12 | 40.12 | [9 empty] | 0.59 | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.33 |  | 30 | M. Usman | 正常
2021.05.07 | 37.9 | 38.7 | 40.5 | 38 | 37.12 | 42 | 41 | 41 | 45 | 43.1 | 45.3 | 1 | 40.3 | 39.5 | 42.3 | 41.45 | 40.12 | 43.76 | 43 | 42 | 46 | 44.5 | 44.9 | 1 | 36.4 | 35.8 | 41.6 | 39.07 | 39.5 | 41.69 | 40 | 40 | 45 | 37.8 | 38.1 | 1 | 38.1 | 38.2 | 39.3 | 38.75 | 38.84 | 40.24 | 40 | 41 | 42 | 41.5 | 47.2 | 1 | 39 | 38.7 | 39.3 | 39.93 | 39.23 | 40.16 | 40 | 41 | 42 | 44.5 | 45.5 | 1 | 38.8 | 38.4 | 39.5 | 39.69 | 38.99 | 40.44 | 42 | 42 | 43 | 39.4 | 45.6 | 1 | 0.589 | 0.34 | 0.35 | 0.34 | 0.345 | 0.34 | 0.34 | 0.35 | 0.35 | 0.343 | 0.344 | 0.33 | 0.334 | -390 | 30 | Abdullah & Abu Bakar | 正常
2021.05.08 | 39 | 41 | 42 | [9 empty] | 43 | 42 | 43 | [9 empty] | 39 | 41 | 42 | [9 empty] | 39 | 38 | 40 | [9 empty] | 39 | 39 | 41 | [9 empty] | 41 | 42 | 41 | [9 empty] | 0.588 | 0.34 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.35 | 0.34 | 0.34 | 0.33 | 0.33 | -390 | 30 | Rehan | 正常
2021.05.09 | 39.6 | 39.5 | 40.5 | [9 empty] | 40.9 | 39.3 | 41.1 | [9 empty] | 40.4 | 38.9 | 42.5 | [9 empty] | 39.3 | 38.8 | 39.7 | [9 empty] | 39 | 38 | 39 | [9 empty] | 39.4 | 38.4 | 39.5 | [9 empty] | 0.588 | 0.34 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.35 | 0.34 | 0.34 | 0.33 | 0.33 | -390 | 32 | Abdullah & Abu Bakar | 正常
2021.05.10 | 40 | 38 | 43 | [9 empty] | 41 | 39 | 42 | [9 empty] | 40 | 40 | 42 | [9 empty] | 40 | 39 | 40 | [9 empty] | 40 | 39 | 40 | [9 empty] | 40 | 40 | 39 | [9 empty] | 0.589 | 0.34 | 0.35 | 0.34 | 0.345 | 0.34 | 0.34 | 0.35 | 0.35 | 0.343 | 0.344 | 0.33 | 0.334 | -390 | 34 | Zubair Tufail | 正常
2021.05.11 | 37.6 | 37.2 | 38.1 | [9 empty] | 39.03 | 37.19 | 38.75 | [9 empty] | 38.05 | 36.25 | 39.73 | [9 empty] | 37.1 | 36.25 | 37.3 | [9 empty] | 39.3 | 37.7 | 38 | [9 empty] | 39.1 | 37.7 | 38 | [9 empty] | 0.588 | 0.35 | 0.349 | 0.346 | 0.346 | 0.345 | 0.344 | 0.346 | 0.347 | 0.341 | 0.334 | 0.327 | 0.333 | -387 | 30 | Zubair Tufail | 正常
2021.05.12 | 38 | 38.5 | 38.5 | [9 empty] | 37.8 | 39.3 | 39.4 | [9 empty] | 36.9 | 40 | 38.3 | [9 empty] | 37.3 | 38.4 | 38.1 | [9 empty] | 40.7 | 40.4 | 42 | [9 empty] | 40.3 | 40.4 | 42.1 | [9 empty] | 0.589 | 0.35 | 0.35 | 0.356 | 0.33 | 0.34 | 0.34 | 0.33 | 0.34 | 0.34 | 0.33 | 0.32 | 0.33 | 394 | 28 | Muhammad Usman | 正常
2021.05.13 | 34.22 | 33.99 | 31.72 | [9 empty] | 35.2 | 33.64 | 31.92 | [9 empty] | 33.64 | 31.96 | 31.76 | [9 empty] | 34.18 | 32.62 | 31.13 | [9 empty] | 34.81 | 32.86 | 30.71 | [9 empty] | 33.5 | 31.7 | 30 | [9 empty] | 0.589 | 0.36 | 0.36 | 0.36 | 0.35 | 0.35 | 0.35 | 0.36 | 0.36 | 0.36 | 0.34 | 0.34 | 0.34 | 394 | 29 | Muhammad Usman | 正常
2021.05.14 | 38.8 | 38.7 | 38.7 | 39.97 | 39.07 | 39.5 | 40 | 40 | 40 | 43.7 | 45.9 | 1 | 39.9 | 38.6 | 39.7 | 41.14 | 39.93 | 39.54 | 40 | 40 | 40 | 44.6 | 45.1 | 1 | 39.2 | 38 | 40.6 | 40.4 | 40.98 | 38.95 | 40 | 40 | 40 | 39.6 | 38.6 | 1 | 39.4 | 38.2 | 38.8 | 40.51 | 39.34 | 39.42 | 40 | 40 | 40 | 41.1 | 45.9 | 1 | 41.7 | 40.2 | 39 | 40.55 | 38.41 | 38.95 | 40 | 42 | 38 | 44.6 | 45.6 | 1 | 41.8 | 40 | 39 | 40.28 | 38.41 | 38.68 | 40 | 40 | 40 | 38.6 | 45.7 | 1 | 0.59 | 0.34 | 0.35 | 0.34 | 0.35 | 0.34 | 0.34 | 0.35 | 0.355 | 0.35 | 0.345 | 0.335 | 0.335 | -381 | 28 | ASAD ALI | 正常
2021.05.15 | 41.9 | 40.9 | 46.3 | [9 empty] | 43.7 | 45.2 | 42.3 | [9 empty] | 42.9 | 43.1 | 45.1 | [9 empty] | 43.3 | 42.5 | 42.3 | [9 empty] | 44.4 | 42.9 | 41.9 | [9 empty] | 44.1 | 42.6 | 42.3 | [9 empty] | 0.588 | 0.34 | 0.35 | 0.34 | 0.35 | 0.34 | 0.34 | 0.35 | 0.35 | 0.35 | 0.34 | 0.33 | 0.33 | -382 | 35 | Abdullah & Zubair | 正常
2021.05.16 | 41.1 | 41.6 | 44.1 | [9 empty] | 41.8 | 40.7 | 44.3 | [9 empty] | 39.5 | 38.4 | 45.7 | [9 empty] | 42.1 | 41.8 | 43.2 | [9 empty] | 40.2 | 39.9 | 41.7 | [9 empty] | 42.4 | 42 | 43.1 | [9 empty] | 0.585 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | 0.34 | 0.33 | 0.33 | 0.32 | 0.32 | 243 | 35 | Adeel & Ashraf | 正常
2021.05.17 | 39.1 | 39.3 | 41.3 | [9 empty] | 40.9 | 39.5 | 42.3 | [9 empty] | 40.1 | 38.6 | 44.3 | [9 empty] | 38.8 | 37.9 | 39.3 | [9 empty] | 39.8 | 38.2 | 39.5 | [9 empty] | 39.5 | 38.6 | 39.5 | [9 empty] | 0.589 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.34 | 0.33 | 0.34 | 0.33 | 0.34 | 0.33 | 0.32 | -387.5 | 35 | Abdullah & Zubair | 正常
2021.05.18 | 40.5 | 40.44 | 42.5 | [9 empty] | 41.76 | 40.12 | 43.68 | [9 empty] | 40.98 | 39.5 | 45.08 | [9 empty] | 40.86 | 40.28 | 40.86 | [9 empty] | 40.82 | 39.58 | 41.1 | [9 empty] | 40.94 | 39.85 | 41.3 | [9 empty] | 0.58 | 0.34 | 0.34 | 0.345 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.32 | 0.33 | -388.9 | 38 | Muhammad Usman | 正常
2021.05.19 | 39.5 | 38 | 41.6 | [8 empty] | 2 | 39.9 | 38.4 | 40.5 | [8 empty] | 2 | 38.5 | 38 | 39.3 | [8 empty] | 2 | 38.4 | 37.5 | 38.4 | [8 empty] | 2 | 38.8 | 37.2 | 38.4 | [8 empty] | 2 | 39.1 | 37.8 | 38.8 | [8 empty] | 2 | 0.59 | 0.34 | 0.35 | 0.341 | 0.342 | 0.34 | 0.33 | 0.341 | 0.342 | 0.33 | 0.34 | 0.33 | 0.32 | -389 | 29.8 | Ahmad Usman | 正常
2021.05.20 | 39.69 | 39.92 | 40.47 | [9 empty] | 39.61 | 38.68 | 40.52 | [9 empty] | 36.91 | 35.55 | 40.63 | [9 empty] | 38.67 | 37.85 | 38.4 | [9 empty] | 40.31 | 38.64 | 38.71 | [9 empty] | 39.96 | 38.36 | 39.26 | [9 empty] | 0.59 | 0.34 | 0.349 | 0.346 | 0.347 | 0.345 | 0.344 | 0.347 | 0.348 | 0.343 | 0.335 | 0.329 | 0.335 | -386.8 | 29.8 | Muhammad Usman | 正常
2021.05.21 | 37.3 | 37.2 | 39.3 | 37.62 | 37.82 | 39.58 | 40 | 39 | 42 | 43.2 | 45.6 | 2 | 39 | 37.4 | 40.2 | 38.68 | 37.78 | 40.87 | 40 | 40 | 42 | 43.5 | 44.6 | 2 | 38 | 36.5 | 41.3 | 38.56 | 37.19 | 41.88 | 40 | 39 | 43 | 38.8 | 38.2 | 2 | 38.8 | 37.9 | 38.8 | 39.07 | 38.48 | 39.07 | 40 | 41 | 40 | 41.2 | 47.5 | 1 | 39.7 | 38 | 38.7 | 40.2 | 38.7 | 39.2 | 40 | 42 | 40 | 44.5 | 45.6 | 1 | 39.7 | 38.1 | 39 | 40.2 | 38.9 | 39.5 | 41 | 41 | 42 | 38.8 | 45.6 | 1 | 0.591 | 0.353 | 0.351 | 0.349 | 0.348 | 0.348 | 0.346 | 0.351 | 0.35 | 0.346 | 0.337 | 0.332 | 0.337 | -386.7 | 28.7 | Ahmad Usman | 正常
2021.05.22 | 41.5 | 45.6 | 41.7 | [9 empty] | 41.2 | 46 | 42.6 | [9 empty] | 40.5 | 46.7 | 41.2 | [9 empty] | 44.2 | 44.2 | 45.2 | [9 empty] | 42.4 | 42.2 | 43.7 | [9 empty] | 42.7 | 42.8 | 43.5 | [9 empty] | 0.59 | 0.349 | 0.348 | 0.345 | 0.345 | 0.344 | 0.342 | 0.346 | 0.346 | 0.343 | 0.336 | 0.329 | 0.335 | 391 | 37 | Rehan Majeed | 正常
2021.05.23 | 37.7 | 37.5 | 38 | [9 empty] | 36.8 | 38 | 37.9 | [9 empty] | 36.3 | 35.2 | 39.2 | [9 empty] | 36.8 | 35.7 | 36.6 | [9 empty] | 38.9 | 37.3 | 36.6 | [9 empty] | 38 | 36.6 | 37.4 | [9 empty] | 0.592 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.35 | 0.35 | 0.34 | 0.33 | 0.33 | 0.33 | -378.1 | 28 | Abdullah Rashid | 正常
2021.05.24 | 41.45 | 41.61 | 42.54 | [9 empty] | 39.76 | 38.48 | 41.41 | [9 empty] | 38.32 | 36.92 | 42.7 | [9 empty] | 41.49 | 40.67 | 41.49 | [9 empty] | 42.54 | 40.83 | 41.33 | [9 empty] | 41.68 | 40.16 | 40.98 | [9 empty] | 0.59 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.35 | 0.32 | 0.33 | -388.9 | 35 | Muhammad Usman | 正常
2021.05.25 | 40.6 | 39.2 | 45.5 | [8 empty] | 2 | 40.6 | 39.3 | 44 | [8 empty] | 2 | 41.1 | 41.3 | 43.9 | [8 empty] | 2 | 40.8 | 41.7 | 40.8 | [8 empty] | 2 | 41.1 | 39.9 | 41.3 | [8 empty] | 2 | 40.4 | 39.2 | 41.3 | [8 empty] | 2 | 0.587 | 0.341 | 0.342 | 0.339 | 0.34 | 0.33 | 0.33 | 0.33 | 0.344 | 0.33 | 0.32 | 0.32 | 0.32 | -386.1 | 32.5 | Ahmad Usman | 正常
2021.05.26 | 42.27 | 42.23 | 44.73 | [9 empty] | 42.19 | 40.59 | 45.08 | [9 empty] | 41.29 | 39.81 | 46.41 | [9 empty] | 41.68 | 41.25 | 42.93 | [9 empty] | 41.29 | 40.75 | 42.66 | [9 empty] | 41.33 | 40.47 | 42.82 | [9 empty] | 0.586 | 0.34 | 0.34 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.327 | 0.33 | -387.2 | 38 | Muhammad Usman | 正常
2021.05.27 | 42.9 | 42.7 | 45.3 | [9 empty] | 42.4 | 41.2 | 45.4 | [9 empty] | 41.5 | 40.1 | 46.2 | [9 empty] | 42.7 | 42.2 | 43.6 | [9 empty] | 42.8 | 41.6 | 42.9 | [9 empty] | 42.2 | 41.4 | 43.2 | [9 empty] | 0.587 | 0.346 | 0.346 | 0.344 | 0.344 | 0.343 | 0.342 | 0.344 | 0.345 | 0.34 | 0.333 | 0.326 | 0.333 | -385.9 | 33.8 | Zubair Tufail | 正常
2021.05.28 | 45.6 | 45.9 | 47.7 | 43.83 | 43.13 | 44.73 | 46 | 45 | 47 | 47.6 | 47.6 | 2 | 46.1 | 44.7 | 48.4 | 44.34 | 42.86 | 45.89 | 45 | 45 | 48 | 47.6 | 45.9 | 2 | 42.8 | 41.4 | 48.8 | 44.19 | 40.2 | 46.3 | 43 | 43 | 48 | 42.1 | 40.3 | 3 | 46.4 | 46 | 46.6 | 43.52 | 42.94 | 44.3 | 46 | 46 | 45 | 44.3 | 48.1 | 2 | 45.6 | 44.5 | 45.8 | 43.72 | 42.66 | 43.56 | 44 | 46 | 45 | 47.5 | 45.5 | 2 | 46.7 | 45.7 | 46.4 | 44.03 | 42.62 | 44.07 | 46 | 46 | 48 | 47.6 | 47.3 | 2 | 0.586 | 0.33 | 0.35 | 0.34 | 0.35 | 0.325 | 0.33 | 0.34 | 0.348 | 0.34 | 0.34 | 0.34 | 0.34 | -386.3 | 38 | Abu Bakar | 正常
2021.05.29 | 45.4 | 43.5 | 45.4 | [9 empty] | 47.1 | 43.7 | 46.5 | [9 empty] | 45.3 | 42.2 | 46.6 | [9 empty] | 46 | 43.8 | 45.2 | [9 empty] | 46.7 | 43.5 | 44.2 | [9 empty] | 46.6 | 43.7 | 44.9 | [9 empty] | 0.587 | 0.347 | 0.346 | 0.344 | 0.343 | 0.343 | 0.341 | 0.345 | 0.345 | 0.341 | 0.333 | 0.327 | 0.332 | -774.2 | 37.8 | Zubair Tufail | 正常
2021.05.30 | 39 | 40 | 39.1 | [8 empty] | 2 | 38.6 | 40.9 | 40.3 | [8 empty] | 2 | 37.7 | 41.5 | 39.1 | [8 empty] | 2 | 38.4 | 39.4 | 38.7 | [8 empty] | 2 | 38 | 39.3 | 38.8 | [8 empty] | 2 | 38.1 | 39.6 | 39.1 | [8 empty] | 2 | 0.586 | 0.35 | 0.34 | 0.34 | 0.34 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | -288.7 | 38.3 | Ehzaz | 正常
2021.05.31 | 41.2 | 41.7 | 42.9 | [9 empty] | 42.6 | 41.3 | 44.3 | [9 empty] | 42.2 | 40.8 | 45.4 | [9 empty] | 45.4 | 44.3 | 44.9 | [9 empty] | 41.7 | 40.7 | 41.7 | [9 empty] | 41.8 | 40.6 | 42 | [9 empty] | 0.586 | 0.33 | 0.35 | 0.34 | 0.35 | 0.325 | 0.33 | 0.34 | 0.348 | 0.34 | 0.34 | 0.34 | 0.34 | -385.9 | 35.39 | Zubair Tufail | 正常
2021.06.01 | 35.7 | 36 | 34.6 | [8 empty] | 2 | 36.7 | 36.1 | 35.6 | [8 empty] | 2 | 35.7 | 35.2 | 36.3 | [8 empty] | 2 | 35.3 | 35.2 | 35 | [8 empty] | 2 | 35.6 | 34.6 | 34.3 | [8 empty] | 2 | 35.7 | 34.7 | 34.8 | [8 empty] | 2 | 0.589 | 0.35 | 0.34 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.33 | 0.34 | -188.3 | 38 | Ehzaz | 正常
2021.06.02 | 41.45 | 41.33 | 41.41 | [9 empty] | 42.31 | 41.3 | 41.96 | [9 empty] | 37.97 | 36.6 | 40.63 | [9 empty] | 42.03 | 40.86 | 41.17 | [9 empty] | 41.99 | 40.39 | 40.16 | [9 empty] | 42.03 | 40.44 | 40.39 | [9 empty] | 0.58 | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | -386.3 | 32 | Muhammad Usman | 正常
2021.06.03 | 42.54 | 41.72 | 42.38 | [9 empty] | 42.47 | 42.54 | 43.48 | [9 empty] | 41.25 | 43.01 | 42.77 | [9 empty] | 41.72 | 41.69 | 43.01 | [9 empty] | 41.25 | 41.1 | 43.32 | [9 empty] | 41.37 | 42.97 | 38.17 | [9 empty] | 0.587 | 0.349 | 0.349 | 0.347 | 0.346 | 0.345 | 0.344 | 0.348 | 0.348 | 0.344 | 0.336 | 0.329 | 0.335 | -390 | 35 | Rehan Majeed | 正常
2021.06.04 | 44.3 | 44.7 | 44.5 | [9 empty] | 44.9 | 43.4 | 44.8 | [9 empty] | 44.4 | 43.9 | 45.6 | [9 empty] | 45.6 | 45.4 | 43.4 | [9 empty] | 45.1 | 44.4 | 43.4 | [9 empty] | 44.5 | 44 | 44.1 | [9 empty] | 0.586 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | -196.3 | 37 | Abdullah Rashid | 正常
2021.06.05 | 45.9 | 44.1 | 44.8 | [8 empty] | 3 | 47.4 | 44.3 | 45.9 | [8 empty] | 3 | 46.2 | 43.2 | 46 | [8 empty] | 3 | 46.7 | 44.1 | 45.2 | [8 empty] | 3 | 47.4 | 44.1 | 44.5 | [8 empty] | 3 | 46.5 | 43.6 | 44.6 | [8 empty] | 3 | 0.597 | 0.345 | 0.344 | 0.343 | 0.341 | 0.341 | 0.339 | 0.343 | 0.344 | 0.339 | 0.331 | 0.325 | 0.331 | -779 | 36 | Abu Bakar | 正常
2021.06.06 | 42.9 | 41.6 | 42.9 | [9 empty] | 44.1 | 41.2 | 43.8 | [9 empty] | 43.1 | 40.7 | 44 | [9 empty] | 42.9 | 40.9 | 42.1 | [9 empty] | 43.8 | 41 | 42.8 | [9 empty] | 43.5 | 41.2 | 42.9 | [9 empty] | 0.586 | 0.35 | 0.35 | 0.348 | 0.347 | 0.347 | 0.345 | 0.348 | 0.349 | 0.344 | 0.336 | 0.33 | 0.336 | -684 | 35.9 | Zubair Tufail | 正常
2021.06.07 | 44.6 | 43.1 | 45.1 | [8 empty] | 3 | 45.1 | 42 | 45.4 | [8 empty] | 3 | 43.6 | 40.7 | 45.8 | [8 empty] | 3 | 44.6 | 42.3 | 44.2 | [8 empty] | 3 | 45.6 | 42.9 | 44.5 | [8 empty] | 3 | 45.1 | 42.7 | 44.3 | [8 empty] | 3 | 0.589 | 0.345 | 0.345 | 0.344 | 0.342 | 0.342 | 0.339 | 0.343 | 0.343 | 0.339 | 0.339 | 0.325 | 0.33 | -686 | 34 | Abu Bakar | 正常
2021.06.08 | 48.4 | 46.4 | 48.9 | [8 empty] | 3 | 49.6 | 46.1 | 49.3 | [8 empty] | 3 | 47.4 | 44.5 | 49.5 | [8 empty] | 3 | 48.2 | 45.6 | 46.9 | [8 empty] | 3 | 50 | 46.5 | 47.9 | [8 empty] | 3 | 49.4 | 46.3 | 47.2 | [8 empty] | 3 | 0.588 | 0.333 | 0.336 | 0.332 | 0.333 | 0.331 | 0.332 | 0.331 | 0.334 | 0.326 | 0.32 | 0.312 | 0.32 | -780.6 | 38 | Abdullah Rashid | 正常
2021.06.09 | 50.5 | 47.6 | 49.9 | [8 empty] | 3 | 51.3 | 46.7 | 50.4 | [8 empty] | 3 | 49.5 | 45.6 | 50.5 | [8 empty] | 3 | 50 | 46.6 | 47.8 | [8 empty] | 3 | 52.3 | 47.6 | 48.8 | [8 empty] | 3 | 51.6 | 47.5 | 48.3 | [8 empty] | 3 | 0.592 | 0.341 | 0.341 | 0.339 | 0.338 | 0.339 | 0.336 | 0.34 | 0.34 | 0.334 | 0.326 | 0.32 | 0.326 | -974 | 36 | Abu Bakar | 正常
2021.06.10 | 53 | 49.9 | 52 | [9 empty] | 53.7 | 48.8 | 52.7 | [9 empty] | 52 | 47.7 | 52.5 | [9 empty] | 53.2 | 49.3 | 50.3 | [9 empty] | 55 | 50.1 | 51 | [9 empty] | 54.6 | 50.3 | 50.6 | [9 empty] | 0.588 | 0.346 | 0.345 | 0.344 | 0.342 | 0.343 | 0.34 | 0.344 | 0.342 | 0.339 | 0.33 | 0.325 | 0.33 | -974.6 | 37 | Zubair Tufail | 正常
2021.06.11 | 48.4 | 45.3 | 46.2 | 47.23 | 44.5 | 45.09 | 50 | 47 | 47 | 48.4 | 47.6 | 2 | 47.4 | 46.5 | 46.5 | 46.96 | 44.33 | 45.44 | 49 | 45 | 47 | 48.5 | 45.8 | 3 | 47.7 | 46.7 | 47 | 47.12 | 42.94 | 45.95 | 48 | 45 | 48 | 42.8 | 40.2 | 2 | 49.1 | 45.7 | 46.1 | 47.27 | 43.99 | 44.68 | 49 | 46 | 46 | 43.4 | 50.6 | 2 | 50.2 | 45.6 | 46 | 48.4 | 44.11 | 44.89 | 46 | 50 | 45 | 48.2 | 45.6 | 2 | 50 | 45.7 | 46.1 | 47.9 | 43.68 | 44.66 | 49 | 46 | 47 | 42.4 | 46.9 | 2 | 0.589 | 0.34 | 0.35 | 0.34 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.348 | 0.34 | 0.335 | 0.335 | -877 | 36 | Rehan Majeed & Abu Bakar | 正常
2021.06.12 | 43.9 | 41.5 | 43.6 | [9 empty] | 45.1 | 41.4 | 44.1 | [9 empty] | 43.8 | 41 | 44.8 | [9 empty] | 44.6 | 41.5 | 42.9 | [9 empty] | 45.9 | 42.4 | 43.1 | [9 empty] | 46 | 42.6 | 43.2 | [9 empty] | 0.589 | 0.352 | 0.352 | 0.351 | 0.349 | 0.349 | 0.346 | 0.35 | 0.349 | 0.346 | 0.337 | 0.331 | 0.336 | -779 | 34.8 | Shamaas | 正常
2021.06.13 | 38.5 | 39.1 | 39 | [9 empty] | 38.8 | 38.7 | 39.8 | [9 empty] | 37.9 | 38 | 37.9 | [9 empty] | 38.2 | 38.3 | 38.4 | [9 empty] | 39.2 | 38.4 | 38.6 | [9 empty] | 38.3 | 38.1 | 38.4 | [9 empty] | 0.595 | 0.36 | 0.361 | 0.36 | 0.358 | 0.358 | 0.356 | 0.36 | 0.359 | 0.355 | 0.346 | 0.342 | 0.346 | -190 | 31 | Rehan Majeed | 正常
2021.06.14 | 40.2 | 38.6 | 39.3 | [9 empty] | 41.5 | 38.7 | 40.4 | [9 empty] | 45.6 | 43.1 | 44.1 | [9 empty] | 45.1 | 42.4 | 41.7 | [9 empty] | 47.4 | 43.9 | 42.5 | [9 empty] | 46.8 | 43.9 | 42.9 | [9 empty] | 0.595 | 0.353 | 0.354 | 0.352 | 0.351 | 0.349 | 0.347 | 0.351 | 0.351 | 0.346 | 0.338 | 0.332 | 0.338 | -682.7 | 28.3 | Zubair Tufail | 正常
2021.06.15 | 42.3 | 41.5 | 42.3 | [9 empty] | 43.7 | 41.7 | 43.2 | [9 empty] | 42.5 | 41 | 44.2 | [9 empty] | 43 | 41.8 | 42.1 | [9 empty] | 43.5 | 41.4 | 42.5 | [9 empty] | 42.9 | 40.7 | 41.3 | [9 empty] | 0.596 | 0.34 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | -980 | 32.5 | Ehzaz | 正常
2021.06.16 | 40.2 | 40.1 | 40.8 | [9 empty] | 40.7 | 39.7 | 41 | [9 empty] | 38.6 | 37.7 | 41.1 | [9 empty] | 40.3 | 38.9 | 39.4 | [9 empty] | 41.6 | 39.6 | 40.2 | [9 empty] | 41.7 | 40 | 40.1 | [9 empty] | 0.588 | 0.352 | 0.354 | 0.352 | 0.351 | 0.35 | 0.348 | 0.352 | 0.352 | 0.347 | 0.339 | 0.333 | 0.339 | -487 | 30.5 | Shamaas | 正常
2021.06.17 | 42 | 42.4 | 44.1 | [8 empty] | 1 | 41.5 | 40.9 | 43.6 | [8 empty] | 2 | 40.7 | 40.5 | 44.9 | [8 empty] | 2 | 42.3 | 42.5 | 43 | [8 empty] | 1 | 42.8 | 42.7 | 42.6 | [8 empty] | 1 | 42.3 | 42.1 | 42.5 | [8 empty] | 1 | 0.587 | 0.343 | 0.345 | 0.343 | 0.343 | 0.341 | 0.341 | 0.343 | 0.344 | 0.339 | 0.331 | 0.325 | 0.331 | -193.7 | 36 | Abu Bakar | 正常
2021.06.18 | 42.1 | 41.5 | 44.7 | 41.4 | 41.9 | 45.3 | 44 | 44 | 49 | 46 | 47 | 2 | 43.4 | 42.7 | 46.1 | 43.8 | 42.8 | 46.7 | 46 | 46 | 49 | 46 | 45 | 2 | 42.1 | 42 | 47.4 | 43.1 | 42.7 | 48.1 | 46 | 47 | 51 | 40 | 39 | 2 | 44.2 | 44.2 | 44.6 | 44.9 | 44.5 | 44.9 | 46 | 48 | 47 | 42 | 50 | 2 | 44.7 | 43.9 | 44.5 | 44.6 | 43.7 | 44.9 | 46 | 46 | 46 | 48 | 44 | 2 | 44.8 | 44 | 44.6 | 44.93 | 44.3 | 44.66 | 48 | 48 | 47 | 41 | 47 | 2 | 0.587 | 0.352 | 0.354 | 0.352 | 0.351 | 0.35 | 0.348 | 0.352 | 0.352 | 0.347 | 0.339 | 0.333 | 0.339 | -241.6 | 36.1 | Zubair Tufail | 正常
2021.06.19 | 41.7 | 41.9 | 45 | [9 empty] | 43.4 | 42.3 | 45.7 | [9 empty] | 42.5 | 42 | 47.4 | [9 empty] | 42.9 | 42.5 | 43.6 | [9 empty] | 43.2 | 42 | 43.3 | [9 empty] | 42.9 | 42.1 | 43.2 | [9 empty] | 0.588 | 0.342 | 0.344 | 0.341 | 0.341 | 0.34 | 0.338 | 0.343 | 0.343 | 0.339 | 0.331 | 0.325 | 0.33 | -788 | 38 | Rehan Majeed | 正常
2021.06.20 | 39.6 | 39.2 | 41.7 | [9 empty] | 41.3 | 40 | 42 | [9 empty] | 39.7 | 38.9 | 43.2 | [9 empty] | 40 | 39.5 | 40.8 | [9 empty] | 40.1 | 39.3 | 40.4 | [9 empty] | 40.2 | 39.3 | 41 | [9 empty] | 0.589 | 0.348 | 0.349 | 0.348 | 0.346 | 0.346 | 0.344 | 0.349 | 0.348 | 0.345 | 0.336 | 0.33 | 0.335 | -290.6 | 32 | Kashif | 正常
2021.06.21 | 39.3 | 38.8 | 41.9 | [9 empty] | 40.9 | 40.2 | 42.9 | [9 empty] | 40.1 | 39.2 | 44.3 | [9 empty] | 40.3 | 39.8 | 41.1 | [9 empty] | 41.4 | 40.7 | 41.3 | [9 empty] | 41.4 | 40.6 | 41.6 | [9 empty] | 0.588 | 0.347 | 0.35 | 0.347 | 0.346 | 0.345 | 0.344 | 0.348 | 0.349 | 0.344 | 0.336 | 0.329 | 0.335 | -290 | 32 | ASAD ALI | 正常
2021.06.22 | 42.3 | 41.5 | 43.9 | [9 empty] | 44.1 | 42 | 44.8 | [9 empty] | 42.8 | 41.4 | 45.8 | [9 empty] | 42.7 | 41 | 42.6 | [9 empty] | 43.6 | 41.1 | 42.7 | [9 empty] | 44.1 | 42.1 | 43.1 | [9 empty] | 0.587 | 0.343 | 0.345 | 0.343 | 0.343 | 0.341 | 0.341 | 0.343 | 0.344 | 0.339 | 0.331 | 0.325 | 0.331 | -586 | 32.7 | Zubair Tufail | 正常
2021.06.23 | 47.7 | 47.7 | 46.2 | [9 empty] | 49.1 | 46.4 | 49 | [9 empty] | 46.2 | 43.8 | 49.7 | [9 empty] | 48.6 | 46.3 | 47.2 | [9 empty] | 49 | 46.2 | 47 | [9 empty] | 49.1 | 46.3 | 46.6 | [9 empty] | 0.588 | 0.338 | 0.34 | 0.338 | 0.338 | 0.337 | 0.336 | 0.337 | 0.338 | 0.334 | 0.326 | 0.32 | 0.326 | -687 | 37 | Rehan Majeed | 正常
2021.06.24 | 45.1 | 43.8 | 45 | [9 empty] | 46.2 | 43.9 | 46.2 | [9 empty] | 45.6 | 43.9 | 47.6 | [9 empty] | 46 | 44.1 | 44.9 | [9 empty] | 48.3 | 45.4 | 45.7 | [9 empty] | 46 | 43.7 | 44.6 | [9 empty] | 0.587 | 0.343 | 0.345 | 0.343 | 0.343 | 0.341 | 0.341 | 0.343 | 0.344 | 0.339 | 0.331 | 0.325 | 0.331 | -683.5 | 32.6 | Zubair Tufail | 正常
2021.06.25 | 51.1 | 48.8 | 49.6 | [8 empty] | 2 | 50.6 | 47.3 | 48.9 | [8 empty] | 3 | 49.1 | 46.3 | 48.4 | [8 empty] | 4 | 50 | 47.4 | 49 | [8 empty] | 3 | 52.5 | 48 | 49.3 | [8 empty] | 2 | 53 | 48.8 | 49.1 | [8 empty] | 2 | 0.595 | 0.339 | 0.34 | 0.339 | 0.337 | 0.338 | 0.335 | 0.339 | 0.339 | 0.336 | 0.327 | 0.321 | 0.327 | -778.4 | 36 | Abu Bakar | 正常
2021.06.26 | 40 | 38.9 | 39.9 | [9 empty] | 41.6 | 39.3 | 41 | [9 empty] | 40.4 | 38.9 | 41.9 | [9 empty] | 40.3 | 38.2 | 39.4 | [9 empty] | 41 | 38.4 | 39.2 | [9 empty] | 40.5 | 38.1 | 38.9 | [9 empty] | 0.59 | 0.353 | 0.355 | 0.353 | 0.351 | 0.351 | 0.348 | 0.352 | 0.353 | 0.348 | 0.34 | 0.334 | 0.339 | -584 | 30 | ASAD ALI | 正常
2021.06.27 | 42.3 | 42.4 | 44.5 | [9 empty] | 42.8 | 41.4 | 45.4 | [9 empty] | 42.5 | 41.1 | 47.1 | [9 empty] | 42.3 | 41.9 | 42.3 | [9 empty] | 42.5 | 41.4 | 42.9 | [9 empty] | 42.5 | 41.7 | 43.4 | [9 empty] | 0.589 | 0.345 | 0.347 | 0.345 | 0.344 | 0.343 | 0.341 | 0.345 | 0.345 | 0.342 | 0.333 | 0.327 | 3.333 | -391 | 35 | Rehan Majeed | 正常
2021.06.28 | 47.7 | 45.6 | 47.2 | [9 empty] | 48.3 | 45.2 | 48.1 | [9 empty] | 45.3 | 42.2 | 48.5 | [9 empty] | 47.5 | 45 | 46.1 | [9 empty] | 48.2 | 44.8 | 45.9 | [9 empty] | 47.5 | 44.6 | 45.8 | [9 empty] | 0.588 | 0.343 | 0.344 | 0.343 | 0.341 | 0.342 | 0.34 | 0.343 | 0.343 | 0.34 | 0.331 | 0.326 | 0.331 | -780 | 36 | ASAD ALI | 正常
2021.06.29 | 42.3 | 42.4 | 44.5 | [9 empty] | 42.8 | 41.4 | 45.4 | [9 empty] | 42.5 | 41.1 | 47.1 | [9 empty] | 42.3 | 41.9 | 42.3 | [9 empty] | 42.5 | 41.4 | 42.9 | [9 empty] | 42.5 | 41.7 | 43.4 | [9 empty] | 0.589 | 0.345 | 0.347 | 0.345 | 0.344 | 0.343 | 0.341 | 0.345 | 0.345 | 0.342 | 0.333 | 0.327 | 3.333 | -589 | 35 | Rehan Majeed | 正常
2021.06.30 | 44.8 | 45.9 | 43.1 | [9 empty] | 46.2 | 47.5 | 48.2 | [9 empty] | 45 | 48.2 | 42 | [9 empty] | 46.1 | 46.1 | 44.1 | [9 empty] | 46.8 | 44.9 | 43.6 | [9 empty] | 46.3 | 45.2 | 43.7 | [9 empty] | 0.588 | 0.338 | 0.34 | 0.338 | 0.338 | 0.337 | 0.336 | 0.337 | 0.338 | 0.334 | 0.326 | 0.32 | 0.326 | -731.7 | 34.7 | Zubair Tufail | 正常
2021.07.01 | 45.4 | 43.5 | 45.4 | [9 empty] | 47.1 | 43.7 | 46.5 | [9 empty] | 45.3 | 42.2 | 46.6 | [9 empty] | 46 | 43.8 | 45.2 | [9 empty] | 46.7 | 43.5 | 44.2 | [9 empty] | 46.6 | 43.7 | 44.9 | [9 empty] | 0.587 | 0.347 | 0.346 | 0.344 | 0.343 | 0.343 | 0.341 | 0.345 | 0.345 | 0.341 | 0.333 | 0.327 | 0.332 | -881 | 39 | Rehan Majeed | 正常
2021.07.02 | 45.4 | 42.4 | 44.7 | 45.71 | 43.13 | 45.67 | 49 | 46 | 48 | 48.5 | 48 | 3 | 46.8 | 42.6 | 45.7 | 47.2 | 43.25 | 46.69 | 49.5 | 46 | 49 | 48.8 | 46 | 3 | 45.6 | 41.9 | 46.7 | 46.53 | 42.7 | 47.86 | 48 | 46 | 50 | 43.4 | 40.7 | 3 | 46.4 | 43 | 44.6 | 46.6 | 43.68 | 45.16 | 48 | 46 | 46.5 | 44.4 | 49.8 | 3 | 46.4 | 42.3 | 43.9 | 46.26 | 42.66 | 44.38 | 44 | 49 | 44 | 47 | 45.6 | 3 | 46 | 42.3 | 43.8 | 46.37 | 42.55 | 44.07 | 48 | 45 | 46 | 42.2 | 47.5 | 3 | 0.588 | 0.338 | 0.34 | 0.338 | 0.338 | 0.337 | 0.336 | 0.337 | 0.338 | 0.334 | 0.326 | 0.32 | 0.326 | -826.7 | 33 | Zubair Tufail | 正常
2021.07.03 | 44.3 | 41 | 42 | [9 empty] | 45.6 | 41.4 | 43.2 | [9 empty] | 44.1 | 40.4 | 44 | [9 empty] | 44.3 | 40.3 | 41.7 | [9 empty] | 45 | 40.5 | 41 | [9 empty] | 44.8 | 40.5 | 41.3 | [9 empty] | 0.597 | 0.35 | 0.532 | 0.352 | 0.349 | 0.35 | 0.348 | 0.351 | 0.35 | 0.347 | 0.338 | 0.332 | 0.337 | -876.2 | 32.6 | Zubair Tufail | 正常
2021.07.04 | 45.4 | 41.5 | 41.6 | [9 empty] | 46.8 | 42 | 42.8 | [9 empty] | 44.1 | 39.5 | 42.8 | [9 empty] | 46 | 41.5 | 42.3 | [9 empty] | 46.7 | 41.4 | 41.6 | [9 empty] | 46.3 | 41.1 | 41.6 | [9 empty] | 0.592 | 0.349 | 0.351 | 0.35 | 0.349 | 0.35 | 0.347 | 0.349 | 0.349 | 0.345 | 0.337 | 0.331 | 0.336 | -974 | 31.4 | Shamaas | 正常
2021.07.05 | 47.5 | 42.8 | 43.6 | [9 empty] | 48.6 | 42.6 | 44.1 | [9 empty] | 47 | 42 | 45.1 | [9 empty] | 47 | 41.8 | 43 | [9 empty] | 48 | 42 | 42.9 | [9 empty] | 47.8 | 42.3 | 42.9 | [9 empty] | 0.59 | 0.347 | 0.35 | 0.349 | 0.347 | 0.347 | 0.345 | 0.348 | 0.348 | 0.344 | 0.336 | 0.33 | 0.335 | -1072 | 34 | ASAD ALI | 正常
2021.07.06 | 48.7 | 44.7 | 46.8 | [9 empty] | 50.1 | 44.6 | 47.8 | [9 empty] | 49.1 | 44.1 | 48.5 | [9 empty] | 49.6 | 44.7 | 45.7 | [9 empty] | 50.2 | 44.1 | 45.8 | [9 empty] | 49.5 | 44 | 45.4 | [9 empty] | 0.592 | 0.349 | 0.351 | 0.35 | 0.349 | 0.35 | 0.347 | 0.349 | 0.349 | 0.345 | 0.337 | 0.331 | 0.336 | -1071 | 33 | Shamaas | 正常
2021.07.07 | 50.5 | 46.1 | 48.1 | [9 empty] | 51.3 | 45.4 | 49 | [9 empty] | 50.5 | 45 | 49.5 | [9 empty] | 51 | 45.8 | 46.9 | [9 empty] | 51.3 | 45 | 47 | [9 empty] | 50.9 | 45.2 | 46.9 | [9 empty] | 0.592 | 0.342 | 0.344 | 0.343 | 0.341 | 0.342 | 0.339 | 0.339 | 0.33 | 0.325 | 0.329 | 0.352 | 0.348 | -1070.8 | 32.4 | Zubair Tufail | 正常
2021.07.08 | 50 | 46.1 | 48.6 | [9 empty] | 51.6 | 45.7 | 49 | [9 empty] | 50 | 46 | 49.7 | [9 empty] | 51.3 | 46.8 | 47.5 | [9 empty] | 51.3 | 45.6 | 47 | [9 empty] | 50.6 | 45.7 | 47.2 | [9 empty] | 0.594 | 0.343 | 0.345 | 0.344 | 0.342 | 0.343 | 0.34 | 0.344 | 0.342 | 0.34 | 0.331 | 0.326 | 0.33 | -1022 | 36.6 | Qasim | 正常
2021.07.09 | 45.7 | 42.4 | 43.9 | [9 empty] | 47.7 | 43.3 | 45 | [9 empty] | 46.7 | 42.9 | 45.3 | [9 empty] | 47 | 43 | 44.2 | [9 empty] | 47.6 | 42.7 | 42.9 | [9 empty] | 46.5 | 42.2 | 43.2 | [9 empty] | 0.596 | 0.35 | 0.351 | 0.351 | 0.349 | 0.35 | 0.347 | 0.352 | 0.35 | 0.347 | 0.337 | 0.332 | 0.336 | -924 | 33.1 | Shamaas | 正常
2021.07.10 | 48.6 | 44.3 | 45.4 | [9 empty] | 50 | 44.3 | 46.5 | [9 empty] | 49.1 | 44.1 | 46.6 | [9 empty] | 49.4 | 44.4 | 44.9 | [9 empty] | 49.8 | 43.5 | 44.4 | [9 empty] | 49 | 43.3 | 44.7 | [9 empty] | 0.594 | 0.349 | 0.351 | 0.351 | 0.349 | 0.349 | 0.346 | 0.351 | 0.35 | 0.346 | 0.337 | 0.332 | 0.336 | -1069 | 34 | ASAD ALI | 正常
2021.07.11 | 45.4 | 43.5 | 45 | [8 empty] | 3 | 46.5 | 43.3 | 45.6 | [8 empty] | 3 | 45 | 42.2 | 45.8 | [8 empty] | 3 | 45.4 | 43.5 | 44.2 | [8 empty] | 3 | 46.1 | 43 | 43.9 | [8 empty] | 3 | 45.7 | 43.1 | 44.1 | [8 empty] | 3 | 0.591 | 0.346 | 0.349 | 0.348 | 0.346 | 0.347 | 0.344 | 0.349 | 0.347 | 0.345 | 0.335 | 0.33 | 0.334 | -731 | 36 | Abu Bakar | 正常
2021.07.12 | 40.9 | 40.7 | 39.7 | [9 empty] | 41.3 | 39.9 | 40.1 | [9 empty] | 39.5 | 38.3 | 39.9 | [9 empty] | 40.3 | 39.5 | 39.4 | [9 empty] | 40.7 | 38.7 | 39.3 | [9 empty] | 41.4 | 39.7 | 39.3 | [9 empty] | 0.605 | 0.348 | 0.352 | 0.351 | 0.35 | 0.35 | 0.348 | 0.352 | 0.353 | 0.347 | 0.34 | 0.332 | 0.338 | -288 | 26 | ASAD ALI | 正常
2021.07.13 | 35.3 | 36.1 | 35.6 | [9 empty] | 36 | 35.6 | 35.5 | [9 empty] | 35.2 | 35.2 | 35.5 | [9 empty] | 35.9 | 36.1 | 35.3 | [9 empty] | 38.6 | 37.9 | 35.5 | [9 empty] | 35.9 | 35.6 | 35.4 | [9 empty] | 0.591 | 0.347 | 0.353 | 0.35 | 0.35 | 0.348 | 0.347 | 0.351 | 0.352 | 0.347 | 0.339 | 0.333 | 0.339 | 0 | 39.9 | Zubair Tufail | 正常
2021.07.14 | 38.5 | 38 | 39.3 | [9 empty] | 40 | 38.5 | 40 | [9 empty] | 39.2 | 38 | 41.1 | [9 empty] | 43.2 | 41.5 | 40.6 | [9 empty] | 40.1 | 37.8 | 38 | [9 empty] | 44.5 | 42.3 | 41.3 | [9 empty] | 0.599 | 0.349 | 0.353 | 0.352 | 0.35 | 0.35 | 0.347 | 0.352 | 0.352 | 0.349 | 0.34 | 0.334 | 0.339 | -489 | 27.9 | Shamaas | 正常
2021.07.15 | 39 | 39.5 | 41.4 | [9 empty] | 39.4 | 38.8 | 41.9 | [9 empty] | 38.9 | 38.3 | 43.2 | [9 empty] | 40.9 | 40.9 | 42.1 | [9 empty] | 38,9 | 38.5 | 39.8 | [9 empty] | 39 | 38.4 | 39.8 | [9 empty] | 0.589 | 0.344 | 0.349 | 0.347 | 0.346 | 0.345 | 0.343 | 0.347 | 0.347 | 0.344 | 0.336 | 0.33 | 0.335 | -191 | 31.6 | Shamaas | 正常
2021.07.16 | 41.4 | 41 | 42.2 | 41.72 | 41.74 | 42.86 | 45 | 43 | 46 | 46.8 | 47.3 | 2 | 42.5 | 40.9 | 42.8 | 42.97 | 41.02 | 43.95 | 44 | 44 | 46 | 46.9 | 45.4 | 2 | 41.3 | 40.4 | 44.3 | 41.92 | 40.4 | 44.85 | 44 | 43 | 47 | 41.8 | 39.9 | 2 | 41.5 | 40.3 | 41.4 | 41.76 | 40.59 | 42 | 44 | 43 | 44 | 43.5 | 49 | 2 | 41.6 | 39.7 | 40.7 | 42 | 40.16 | 41.41 | 44 | 43 | 43 | 45.8 | 45.6 | 2 | 41.4 | 39.9 | 41.3 | 42.11 | 40.44 | 42.04 | 44 | 43 | 45 | 40.8 | 46.5 | 2 | 0.59 | 0.343 | 0.347 | 0.346 | 0.344 | 0.344 | 0.342 | 0.347 | 0.347 | 0.343 | 0.335 | 0.329 | 0.334 | -439 | 32 | ASAD ALI | 正常
2021.07.17 | 42.9 | 42.4 | 44.5 | [9 empty] | 44.1 | 42 | 45.1 | [9 empty] | 42.8 | 41.4 | 46.2 | [9 empty] | 42.9 | 41.8 | 42.9 | [9 empty] | 43.2 | 41.1 | 42.6 | [9 empty] | 42.9 | 41.4 | 42.8 | [9 empty] | 0.588 | 0.341 | 0.345 | 0.344 | 0.343 | 0.342 | 0.34 | 0.346 | 0.345 | 0.342 | 0.333 | 0.328 | 0.332 | -488 | 35 | ASAD ALI | 正常
2021.07.18 | 43.7 | 43.1 | 44.8 | [9 empty] | 44.7 | 43.4 | 45.7 | [9 empty] | 43.4 | 42.2 | 46.7 | [9 empty] | 43.3 | 43.1 | 44.6 | [9 empty] | 43.5 | 42.7 | 43.5 | [9 empty] | 43.9 | 43.4 | 44.3 | [9 empty] | 0.588 | 0.341 | 0.344 | 0.343 | 0.341 | 0.342 | 0.339 | 0.345 | 0.343 | 0.341 | 0.332 | 0.326 | 0.331 | -240.6 | 36.5 | Qasim | 正常
2021.07.19 | 42.1 | 41.6 | 43.3 | [9 empty] | 43.4 | 42.1 | 43.8 | [9 empty] | 41.6 | 39.7 | 44.8 | [9 empty] | 42.7 | 41.8 | 42.7 | [9 empty] | 42.8 | 41.4 | 41.9 | [9 empty] | 42.9 | 41.7 | 42.9 | [9 empty] | 0.59 | 0.345 | 0.348 | 0.348 | 0.346 | 0.346 | 0.343 | 0.349 | 0.347 | 0.345 | 0.335 | 0.33 | 0.334 | -388 | 33.6 | Shamaas | 正常
2021.07.20 | 37 | 37.3 | 36.1 | [9 empty] | 36.5 | 36.5 | 35.8 | [9 empty] | 36.1 | 35.9 | 36.7 | [9 empty] | 35.7 | 35.7 | 35.4 | [9 empty] | 37.2 | 36.4 | 35.2 | [9 empty] | 36.7 | 35.6 | 35.7 | [9 empty] | 0.601 | 0.353 | 0.357 | 0.357 | 0.354 | 0.355 | 0.352 | 0.357 | 0.356 | 0.353 | 0.344 | 0.339 | 0.343 | -191 | 28 | ASAD ALI | 正常
2021.07.21 | 37.9 | 38.3 | 39 | [8 empty] | 1 | 38.9 | 38.5 | 39.6 | [8 empty] | 1 | 38 | 38 | 41.1 | [8 empty] | 1 | 34.5 | 34.6 | 34.5 | [8 empty] | 1 | 38 | 37.3 | 37.5 | [8 empty] | 1 | 37.5 | 37 | 37.4 | [8 empty] | 1 | 0.59 | 0.349 | 0.355 | 0.353 | 0.352 | 0.35 | 0.349 | 0.353 | 0.354 | 0.349 | 0.342 | 0.336 | 0.342 | -193 | 26 | Abu Bakar | 正常
2021.07.22 | 40.9 | 41.3 | 42.2 | [9 empty] | 41.3 | 40.9 | 42.9 | [9 empty] | 41 | 41 | 44.7 | [9 empty] | 40.9 | 41.1 | 41.5 | [9 empty] | 41.6 | 40.8 | 41.1 | [9 empty] | 41.1 | 40.5 | 41.3 | [9 empty] | 0.592 | 0.352 | 0.349 | 0.342 | 0.344 | 0.342 | 0.356 | 0.347 | 0.352 | 0.334 | 0.34 | 0.333 | 0.331 | -192 | 29.8 | Zubair Tufail | 正常
2021.07.23 | 39.4 | 39.7 | 40.8 | 41.45 | 41.96 | 43.95 | 44 | 44 | 47 | 45.3 | 46.4 | 2 | 40.5 | 39.7 | 41.3 | 42.11 | 41.02 | 44.19 | 44 | 45 | 46 | 45.5 | 45.1 | 2 | 39.3 | 38.9 | 42 | 41.33 | 40.48 | 45.05 | 44 | 44 | 45 | 40.6 | 39.4 | 2 | 42.3 | 42.2 | 42.4 | 44.3 | 44.15 | 43.99 | 46 | 47 | 46 | 42.4 | 48.8 | 1 | 42.8 | 42 | 41.7 | 44.61 | 43.76 | 43.25 | 46 | 46 | 45 | 45.6 | 45.5 | 1 | 42.3 | 41.7 | 42 | 44.3 | 43.99 | 43.48 | 47 | 48 | 46 | 40.7 | 46.7 | 1 | 0.59 | 0.342 | 0.347 | 0.346 | 0.344 | 0.344 | 0.342 | 0.346 | 0.346 | 0.342 | 0.334 | 0.328 | 0.334 | -192.3 | 31.8 | Zubair Tufail | 正常
2021.07.24 | 40.8 | 41 | 42.9 | [9 empty] | 41.3 | 40.6 | 43.2 | [9 empty] | 40.4 | 39.8 | 44.3 | [9 empty] | 40.6 | 40.4 | 41.7 | [9 empty] | 40.8 | 39.9 | 41.3 | [9 empty] | 40.5 | 39.9 | 41.5 | [9 empty] | 0.589 | 0.34 | 0.346 | 0.344 | 0.343 | 0.342 | 0.34 | 0.345 | 0.346 | 0.341 | 0.333 | 0.327 | 0.333 | -241 | 33 | Shamaas | 正常
2021.07.25 | 42.1 | 41.3 | 42.5 | [8 empty] | 2 | 43.4 | 41.4 | 43.2 | [8 empty] | 2 | 42.5 | 41.1 | 44.3 | [9 empty] | 42.1 | 40.4 | 41.8 | [9 empty] | 42.5 | 40.2 | 41.3 | [9 empty] | 41.7 | 39.9 | 41.3 | [9 empty] | 0.589 | 0.34 | 0.345 | 0.344 | 0.342 | 0.342 | 0.34 | 0.345 | 0.345 | 0.341 | 0.333 | 0.327 | 0.332 | -586.5 | 32 | Shamaas | 正常
2021.07.26 | 42.9 | 42 | 41.8 | [8 empty] | 2 | 44.8 | 42.6 | 43.2 | [8 empty] | 2 | 43.6 | 41.6 | 44.6 | [8 empty] | 2 | 42.9 | 41.3 | 42.1 | [8 empty] | 2 | 43.9 | 41.1 | 41.3 | [8 empty] | 2 | 43.1 | 41.1 | 41.6 | [8 empty] | 2 | 0.592 | 0.344 | 0.349 | 0.348 | 0.346 | 0.346 | 0.343 | 0.349 | 0.348 | 0.345 | 0.336 | 0.33 | 0.335 | -585.8 | 33.5 | Qasim | 正常
2021.07.27 | 43.9 | 41.8 | 42.2 | [9 empty] | 45.7 | 42.6 | 43.5 | [9 empty] | 44.4 | 41.3 | 44.5 | [9 empty] | 44.9 | 41.8 | 42.7 | [9 empty] | 45.3 | 41.7 | 41.9 | [9 empty] | 45.3 | 42 | 42.3 | [9 empty] | 0.594 | 0.347 | 0.352 | 0.35 | 0.349 | 0.349 | 0.346 | 0.351 | 0.351 | 0.347 | 0.339 | 0.332 | 0.337 | -730.5 | 32.3 | Zubair Tufail | 正常
2021.07.28 | 41.4 | 40.4 | 41.4 | [8 empty] | 2 | 43.1 | 40.9 | 42.5 | [8 empty] | 2 | 41.9 | 40.1 | 43.2 | [8 empty] | 2 | 42.1 | 40.4 | 41.5 | [8 empty] | 2 | 42.5 | 40.2 | 41 | [8 empty] | 2 | 42.6 | 40.2 | 41.3 | [8 empty] | 2 | 0.593 | 0.345 | 0.351 | 0.349 | 0.348 | 0.348 | 0.345 | 0.35 | 0.35 | 0.346 | 0.338 | 0.331 | 0.337 | -584.6 | 31.2 | Qasim | 正常
2021.07.29 | 35.6 | 35.7 | 36.1 | [9 empty] | 36.4 | 35.6 | 36.8 | [9 empty] | 35.5 | 35.2 | 38 | [9 empty] | 37.6 | 37.7 | 37.8 | [9 empty] | 38.9 | 37.9 | 37.4 | [9 empty] | 37.5 | 37.3 | 37.2 | [9 empty] | 0.592 | 0.34 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 34 | -193 | 26 | Ashraf | 正常
2021.07.30 | 40.2 | 40.1 | 41.4 | [9 empty] | 41 | 40 | 41.6 | [9 empty] | 40.7 | 39.5 | 42.9 | [9 empty] | 43.5 | 42.2 | 42.3 | [9 empty] | 41.3 | 39.7 | 40.5 | [9 empty] | 40.8 | 39.7 | 41 | [9 empty] | 0.59 | 0.345 | 0.351 | 0.349 | 0.348 | 0.348 | 0.345 | 0.35 | 0.35 | 0.347 | 0.338 | 0.332 | 0.337 | -388 | 32.7 | Shamaas | 正常
2021.07.31 | 40.8 | 40.7 | 42 | [9 empty] | 41.6 | 40.3 | 42.5 | [9 empty] | 41 | 40.1 | 44.3 | [9 empty] | 45.2 | 43.8 | 43.6 | [9 empty] | 42 | 39.9 | 41.1 | [9 empty] | 41.4 | 39.9 | 41.5 | [9 empty] | 0.592 | 0.344 | 0.35 | 0.348 | 0.347 | 0.347 | 0.344 | 0.349 | 0.348 | 0.346 | 0.337 | 0.331 | 0.336 | -437 | 31.9 | Shamaas | 正常
2021.08.01 | 40.2 | 39.7 | 42 | [8 empty] | 2 | 41 | 39.7 | 42.3 | [8 empty] | 2 | 40.4 | 39.5 | 44.1 | [8 empty] | 2 | 44.3 | 42.7 | 43 | [8 empty] | 1 | 41.1 | 39.4 | 40.4 | [8 empty] | 2 | 40.8 | 39.3 | 41 | [8 empty] | 2 | 0.59 | 0.342 | 0.348 | 0.347 | 0.346 | 0.345 | 0.343 | 0.346 | 0.346 | 0.343 | 0.335 | 0.329 | 0.334 | -438.4 | 32.2 | Qasim | 正常
2021.08.02 | 49.3 | 43.5 | 44.5 | [9 empty] | 50.9 | 44 | 45 | [9 empty] | 49.5 | 43.6 | 46.1 | [9 empty] | 49.6 | 43.5 | 43.9 | [9 empty] | 50.5 | 43.2 | 43.9 | [9 empty] | 49.6 | 43.1 | 44.4 | [9 empty] | 0.591 | 0.344 | 0.349 | 0.348 | 0.347 | 0.347 | 0.344 | 0.349 | 0.348 | 0.345 | 0.336 | 0.331 | 0.335 | -1174 | 30 | Shamaas | 正常
2021.08.03 | 42.3 | 40.9 | 42.8 | [9 empty] | 43.4 | 40.9 | 43.4 | [9 empty] | 42.5 | 40.4 | 44.7 | [9 empty] | 46.4 | 44.1 | 43.9 | [9 empty] | 43.5 | 40.5 | 41.4 | [9 empty] | 42.9 | 40.2 | 42 | [9 empty] | 0.591 | 0.345 | 0.351 | 0.35 | 0.348 | 0.348 | 0.346 | 0.349 | 0.349 | 0.346 | 0.338 | 0.331 | 0.337 | -678 | 31.8 | Shamaas | 正常
2021.08.04 | 39.3 | 38.8 | 40.1 | [9 empty] | 40.4 | 39 | 40.7 | [9 empty] | 39.8 | 38.6 | 42 | [9 empty] | 40 | 38.6 | 39.3 | [9 empty] | 40.4 | 38.5 | 39.6 | [9 empty] | 39.9 | 38.1 | 39.8 | [9 empty] | 0.59 | 0.346 | 0.352 | 0.351 | 0.349 | 0.349 | 0.347 | 0.351 | 0.351 | 0.347 | 0.339 | 0.333 | 0.338 | -485 | 29.6 | Shamaas | 正常
2021.08.05 | 44.6 | 42.4 | 43.3 | [9 empty] | 45.7 | 42.3 | 44.4 | [9 empty] | 44.7 | 42.2 | 44.8 | [9 empty] | 44.8 | 42.2 | 42.7 | [9 empty] | 45 | 42 | 42.9 | [9 empty] | 45.1 | 41.9 | 42.9 | [9 empty] | 0.592 | 0.343 | 0.349 | 0.348 | 0.347 | 0.347 | 0.344 | 0.349 | 0.348 | 0.345 | 0.336 | 0.331 | 0.335 | -707 | 33.4 | Shamaas | 正常
2021.08.06
2021.08.07
2021.08.08
2021.08.09
2021.08.10
2021.08.11
2021.08.12
2021.08.13
2021.08.14
2021.08.15
2021.08.16
2021.08.17
2021.08.18
2021.08.19
2021.08.20
2021.08.21
2021.08.22
2021.08.23
2021.08.24
2021.08.25
2021.08.26
2021.08.27
2021.08.28
2021.08.29
2021.08.30