## Sheet1
Sr. No. | Name | Date | Description | System
1 | Abdullah | 2021.05.22 | Found the Air conditioners of pole 1 DC storage Battery room1, pole 2 DC storage battery room 1 and 2 at first floor control building in battery rooms were not working properly reported to Mr YinPisheng | Control Building
2 | Zubair | 2021.05.22 | found the lock of panel pole 1 Y/Y converter transformer Interface A faulty | Control Building
3 | Abdullah | 2021.05.23 | Found the bird nest in the AC yard at various places and also the anbormal voice in the suply box near Lahore Line 1 and told Mr YuPung | AC yard
4 | Abdullah | 2021.05.25 | Found the bird nest in AC yard and also the bug home in control room stairs and told Mr Lee | AC yard
5 | Ahmad | 2021.05.25 | I have found a big unnecessary Screw in AC filter Yard and reported to master | ACF Yard
6 | Abu Bakar | 2021.05.26 | J2 YDA Lightning arrestor Integration Platform data not updated after 24-05-2021, 19:25 | Integration Platform
7 | Abu Bakar | 2021.05.26 | J2 YY Neutral Point MOA Integration Platform data not updated after 24-05-2021, 19:25 | Integration Platform
8 | Rehan | 2021.05.26 | Found a bird nest at arrestor P2-WN-F2 | DC Yard
9 | Rehan | 2021.05.26 | Found a Bee House near WP2Q10 | DC Yard
10 | Rehan | 2021.05.26 | Found broken floor under the stairs of Fire Pump House | Fire Pump House
11 | Rehan | 2021.05.26 | Living water pump leakage betweem two pumps | Living water tank
12 | Rehan | 2021.05.26 | Power supply socket of UV Sterlizer is very near to ground. If there is water, it will be short circuited | Living water tank
13 | Abdullah | 2021.05.27 | Found a big screw and steel bracket at YDB & YDC Pole 2 and reported to the master and sent pictures in the group . | converter transformers area
14 | Abdullah | 2021.05.27 | I found a dead bird in AC Yard and reported to Mr.Lee | AC Yard
15 | Zubair | 2021.05.27 | I found garbage at YDB & YDC Pole 2. | AC Yard
16 | Abu Bakar | 2021.05.28 | Found a Big card board in AC yard near Bay 1 B1Q1 | AC Yard
17 | Abdullah | 2021.05.29 | Found the E3E10 wire insulation was not intact in the 132kV yard and reported to MR lishoujin | AC Yard
18 | Abdullah | 2021.05.29 | Found the dead bird in the ACF yard and some plastic object reported to Mr lishoujin and sent the pictures in group | AC yard
19 | Abdullah | 2021.05.29 | Found the piece of cloth inside the pole 1 neutral smoothing rewactor fence and reported to Mr lishoujin | DC yard
20 | Abdullah | 2021.05.29 | Found the fence lock missing at T5 and also the clay was not intact with control box and 1 Big bolt was also found reported to Mr Lishoujin and sent the pictures in group | AC yard
21 | ASAD ALI | 2021.05.29 | Found the E3E10 wire insulation was not intact in the 132kV yard and reported to MR lishoujin | AC Yard
22 | ASAD ALI | 2021.05.29 | Found the dead bird in the ACF yard and some plastic object reported to Mr lishoujin and sent the pictures in group | AC yard
23 | ASAD ALI | 2021.05.29 | Found the piece of cloth inside the pole 1 neutral smoothing rewactor fence and reported to Mr lishoujin | DC yard
24 | ASAD ALI | 2021.05.29 | Found the fence lock missing at T5 and also the clay was not intact with control box and 1 Big bolt was also found reported to Mr Lishoujin and sent the pictures in group | AC yard
25 | Rehan | 2021.05.28 | Found a Big card board in AC yard near Bay 1 B1Q1 | AC Yard
26 | Zubair | 2021.05.30 | Found the black dog in AC yard | Acyard
27 | Rehan | 2021.05.30 | 51 Realy Room Camera not working properly | Video Record
28 | Abdullah | 2021.05.31 | found the big bird nest at pole 1 line and reprted to Mr Lee and Mr wang teng | DC yard
29 | Abu Bakar | 2021.05.31 | Converter Transformer P2 YY A Winding Temperature Meter Red and Black needle same temperature, Told Mr. Yu Peng | Conv. Traf.
30 | Abu Bakar | 2021.05.31 | Converter Transformer P2 YY A PLC Air Conditioning not working, Told Mr. Yu Peng | Conv. Traf.
31 | Rehan | 2021.05.31 | Found level of living water tank low. And timely informed masters | Water System
32 | Abu Bakar | 2021.06.01 | Converter Transformer P1 YDB C2H2 Value Changed from 0 to 0.1 at 09:20AM 01.06.2021, Reported to master. | Integration Platform
33 | Abdullah | 2021.06.02 | Found one wasp nest at the metallic structure of pole 2 cooling system heat exchanger and reported to Mr Lee | DC Yard
34 | Abdullah | 2021.06.02 | Found bird nest inside the P2WNU1 neutral side DC voltage divider and sent the pictures in the group and also reported to Mr Lishoujin | DC Yard
35 | ASAD ALI | 2021.06.05 | Converter Transformer P1 YYC C2H2 Value Changed from 0 to 0.1 at 17:00 AM 05.06.2021, Reported to master. | Integration Platform
36 | Abu Bakar | 2021.06.05 | AC Filter Yard Bank 3 and 4 Yard lights not working. | ACF Yard
37 | Abdullah | 2021.06.06 | found wasp home at shunt reactor I CTA and reported to master and also sent the pictures in the group | ACF Yard
38 | Abdullah | 2021.06.06 | Found wasp home near the pole 1 YDC converter transformer and reported to the master | ACF Yard
39 | Abdullah | 2021.06.06 | found the metal brackets near the H5Q1 and reported to the master | ACF Yard
40 | Ahmad | 2021.06.08 | Found small nest of yellow bee in T-4 | AC Yard
41 | Ahmad | 2021.06.08 | Found small nest of yellow bee in H6Q1 | AC Yard
42 | Ahmad | 2021.06.08 | 500kV Room #03 the light of a cabinate was not Good and timely reported to the Master | ACF Room
43 | Abdullah | 2021.06.08 | pole 1 YYC C2H2 gas at 0.2ppm found and reported to the master Mr Yuan Maukai and HVAC system 8 power supply fault reported to Mr Lishoujin | Integration Platform and HVAC
44 | Zubair | 2021.06.08 | HVAC system fault was reported to the master related system 8 power supply alarm reported to Mr Lishoujin and also the C2h2 gas value at 0.2ppm reported to Mr Maukai | HVAC Control room and DGA
45 | Abu Bakar | 2021.06.11 | Pole 1 YDB Cooler giving noise | Converter Transformers area
46 | Abu Bakar | 2021.06.11 | 53 Relay room Charger panel Recitifer module temperature high to 71. Reported to master Xiao Xipeng | 53 Relay Room
47 | Ehzaz | 2021.06.11 | pole 2 YYC C2H2 gas at 0.1ppm found and reported to the master Mr Peshion | Integration Platform
48 | Ehzaz | 2021.06.11 | Pole 1 DC Charger Panel 1 temperature goes to 81 degree. I reported to Master Yu Peng | Pole 1 Protection and Control
49 | Ehzaz | 2021.06.13 | TWO BIRDS NEST AND 1 BEE HOME FOUND IN DC YARD TOLD TO XI PENG | DC Yard
50 | Abu Bakar & Rehan | 2021.06.13 | 35kV CB H1Q1 Operation Counter was broken reported it to chinese master Zhan Zhong Yang | 35kV AC Yard area
51 | Rehan | 2021.06.13 | Found a bird nest on B6E31 C phase | 500kV AC yard
52 | ASAD ALI | 2021.06.13 | T4 C2H2 value chnged from 0 to 0.1 PPM | Integration Platform
53 | ASAD ALI | 2021.06.14 | Pole 1 YDC C2H2 value change from 0 to 0.1 told to Mr. Goa | Integration Platform
54 | Abu Bakar & Rehan | 2021.06.15 | Found in 52 Relay room that Line Lahore 2 R11 and R12 panel relays was not reset after last operation, giving indication of Q10 Line ISO. Open. Told Chinese Master | 52 Relay Room
55 | Zubair | 2021.06.16 | Found bird nests in DC Yard Voltage divided pole 1 and pole 2 neutral line. Find alarm of CBF in Relays room no 1 and 2, Find AC fault in Relay room no 1 due to breaker trip. | DC Yard, 52 and 53 Relay rooms
56 | ASAD ALI | 2021.06.21 | AC yard gate was open at night told to Mr. mokia and locked it . | Ac yard
57 | ASAD ALI | 2021.06.23 | C2H2 value of pol1 yyb,yycyda,ydc and pole 2 yyc,ydb and ydc was high told chinese masters. | Integration Platform
58 | Zubair | 2021-06-25 | Found a Dog in AC Yard in front of Convertor Transformers pole 2 and told chinese master. | AC Yard
59 | Zubair | 2021-06-25 | Found Bird Nests in Voltage Dividers of DC Yard and told chinese master. | DC Yard
60 | ASAD ALI | 2021-06-26 | FOUND A Plastic bag in the fan of T3 AND Told the chinese master and taken out with chinese master (Mr Lee) | AC yard
61 | ASAD ALI | 2021-06-26 | Found plastik bages in AC yard DC yard and Filter yard and inside of F4B2 and F2B4 nad taken out with chiense master (Mr Lee) | AC Yard
62 | Zubair | 2021-06-26 | Found plastic bags in AC Yard , DC Yard and Filter Yard inside F4B2 and F2B4 and told Mr.Lee | AC Yard
63 | Zubair | 2021-06-27 | Found Spanner in Transformer T-7 in 132KV Yard and told Mr.Lee. | 132 KV Yard
64 | ASAD ALI | 2021-06-27 | Found waps nests at converter transformet at conservative tank of pole1 YDC and YYC told chinese master and send photo in group . | converter transformers area
65 | ASAD ALI | 2021-06-27 | Found plastic bags behind the fins of fans of pole 2 YDB told the chinese master | converter transformers area
66 | ASAD ALI | 2021-06-27 | Finf High Temperture Alarm of PLC of pole YDA and YYC and told the chinese master (Mr Mookia ) | converter transformers area
67 | Rehan | 2021-06-29 | Found level of C2H2 of P1YDC rise upto 0.7, and reported it to duty incharge | integration platform
68 | Rehan | 2021-06-29 | Found 2 bird nest in AC yard | 500kv ac yard
69 | ASAD ALI | 2021-06-28 | Find abnormal alarm and Data is not updating of cooling sysytem computer told the chinese master Mr yo pang | cooling system Computer
70 | ASAD ALI | 2021-06-30 | POLE 1 YYA C2HC value increase from 0 to 0.7 PPM told my chinese master MR Yo Pang | Integration Platform
71 | Zubair | 2021-06-30 | Found 7 cooling alarms in PLC of Convertor Transformer. | converter transformers area
72 | ASAD ALI | 2021-07-01 | Relay room 3 AC filter 1 operate box 2 time and date is wrong told to Mr. Peshoin | relay room 3
73 | ASAD ALI | 2021-07-01 | name plate of TFD-P2F2B Pole 2 Y/D. Fallen on the ground Send picture in the group | converter transformers area
74 | Zubair | 2021-07-01 | Translated document of operation ticket in english | documentation
75 | Zubair | 2021-07-01 | Assisted team from outside for wireless checking in whole station. | AC, DC Yard and 132 KV Yard
76 | Zubair | 2021-07-03 | AC water dripping in 2nd floor public room battery room no 1. | 2nd floor public room battery room 1
77 | Zubair | 2021-07-03 | 6 bird nests in DC Yard | DC Yard
78 | ASAD ALI | 2021-07-07 | Find Plastic Cup in the Heat Exchenger of pole 2 told the chinise Master and send picture in group | DC Yard
79 | Zubair | 2021-07-12 | Alarm in Pole 1 Communication room 2nd floor control room told chinese master | Pole 1 Communication room
80 | Zubair | 2021-07-12 | Water leakage in Air Conditioning Equipment Room told chinese master | Air Conditioning Equipment Room
81 | Zubair | 2021-07-12 | Spider webs and spider in Air Conditioning Equipment Room told chinese master | Air Conditioning Equipment Room
82 | Zubair | 2021-07-12 | Found a dead crow in front of Pole 1 DC Yard told to chinese master | DC Yard
83 | Zubair | 2021-07-12 | Found a cat and 5 kittens in Pump House told to chinese master | Pump House
84 | Zubair | 2021-07-12 | Found water leakage in DC yard Cooling system in front of Pole 2 and told to chinese Master | DC Yard
85 | ASAD ALI | 2021-07-25 | Find F1B4E11 C Name Plate fallen told to chinise master and send to Gpup Control | AC Yard
86 | ASAD ALI | 2021-07-25 | Find F2B1Q1 C Door Limit Lamp is ON told the chinise Master and send Picrure in Group | AC Yard
87 | ASAD ALI | 2021-07-25 | Found Wasp Nest at F2B1Q1 A at AC Yard | AC Yard
88 | Abdullah | 2021-08-02 | Found some abnormal noise at HVAC system of pole 1 cooling with Mr Yin Pisheng on comprehensive inspection after Bipole high power testing | DC Yard Cooling Area
89 | Abdullah | 2021-08-02 | Found some water leakage at HVAC system of pole 2 cooling with Mr Yin Pisheng on comprehensive inspection after Bipole high power testing | DC Yard Cooling Area
90 | Abdullah | 2021-08-02 | Found some oil Leakage leakage at Pump House cooling with Mr Yin Pisheng on comprehensive inspection after Bipole high power testing | Fire Water Pump House
91 | Abdullah | 2021-08-03 | 51 Battery room 1 had its air condition off. Turned it back ON and set its setting so that in case of power failure it may turn ON back to normal automatically | 51 Relay room
92 | Abdullah | 2021-08-03 | Found alarm on 132kv RELAY ROOM AND reset it | 132kV relay room
93 | Abdullah | 2021-08-03 | Found that pole 2 cooling system basement has rusting on one of motor body because of water droplet falling from rof with Mr Li | pole 2 cooling room
94 | Abdullah | 2021-08-03 | 52 Battery room 1 and 2 Air condition were OFF. Me and Mr Li turned it ON. | 52 Relay Room